## TCO
Total Cost of Ownership - TCO
On this sheet, users can calculate the TCO using equation A.1 from IEC TS 60076-20 for five different transformer designs.
where: | IC is the initial cost of the transformer; this cost may include installation costs such as foundation and erection costs (requires a more sophisticated evaluation);
P0 is the no-load loss (kW) measured at the rated voltage and rated frequency, on the rated tap;
Pk is the load loss (kW) due to the load, measured at the rated current and rated frequency on the rated tap at a reference temperature;
PCS is the total cooling power (kW) needed for operation at the rated power (including three winding operation if any) (note: this variable is set to zero for passively cooled transformer designs);
PC0 is the cooling power (kW) needed for no-load operation (note: this variable is set to zero for passively cooled transformer designs);
A is the cost of capitalisation of no-load losses in cost per kW;
B is the cost of capitalisation of the losses due to load in cost per kW.
Instructions: enter values for each design into the yellow shaded cells.
| Description: | 315 kVA, 3 Phase Oil-filled; 11/0.4 kV DT
| Calculation: | Baseline | Option #1 | Option #2 | Option #3 | Option #4 | Option #5 | Units | Description
| IC (price tendered) | 6000 | 5450 | 9000 |  |  |  | USD | Initial Cost of the transformer
| P0 (core losses) | 1 | 0.64 | 1 |  |  |  | kW | no-load losses (kW) at rated voltaged and frequency
| Pk (load losses) | 3 | 2.8 | 3 |  |  |  | kW | load losses (kW) at rated current and frequency
| PCS (cooling losses) | 0 | 0 | 0 | 0 | 0 | 0 | kW | total cooling power (kW) for operation at the rated power
| PC0 (cooling losses) | 0 | 0 | 0 | 0 | 0 | 0 | kW | total cooling power (kW) for operation at no-load
No CO2 Price | A | 4102.171 | 4102.171 | 4102.171 | 4102.171 | 4102.171 | 4102.171 | $/kW | cost of capitalisation of no-load losses
| B | 1535.6767 | 1535.6767 | 1535.6767 | 1535.6767 | 1535.6767 | 1535.6767 | $/kW | cost of capitalisation of load losses
With CO2 Price | A | 4726.9986 | 4726.9986 | 4726.9986 | 4726.9986 | 4726.9986 | 4726.9986 | $/kW | cost of capitalisation of no-load losses
| B | 1769.5853 | 1769.5853 | 1769.5853 | 1769.5853 | 1769.5853 | 1769.5853 | $/kW | cost of capitalisation of load losses
| TCONoCO2 | 14709.2011 | 12375.2842 | 17709.2011 | 0 | 0 | 0 | USD, total cost of ownership
| TCOWithCO2 | 16035.7546 | 13430.118 | 19035.7546 | 0 | 0 | 0 | USD, total cost of ownership

## Inputs
Inputs to Calculate A&B Factors
Instructions: enter values for each design into the yellow shaded cells.
O0j | 8760 | the operating time of the transformer at year j in hours |  |  | Generation that follows load
ij | 10% | is the real discount rate at year j in per unit (often the Weighted Average Cost of Capital) |  |  | Your % Mix | Description of Technology Used
n | 30 | is the life expectancy of the transformer in years
iCj | 2% | growth rate of electricty prices in excess of inflation, to determine Cj in future years |  |  | 10% | Solar - Photovoltaic
Oaj | 2000 | is the operating time of the transformer at variable load during year j in h; |  |  | 20% | Hydroelectric power
Ofj | 8760 | is the operating time of the transformer at fixed load during year j in h, usually 8 760 h |  |  | 5% | Wind Turbine
Taj | 0.5 | is the share of variable load in the total load loss factor at year j; |  |  | 50% | Natural Gas - Peaking capacity
Tfj | 0.5 | is the share of fixed load in the total load loss factor at year j; |  |  | 15% | Diesel Generator
Cμj | 0 | is the rate of load loss factor increase at year j;
Caj | 0 | is the rate of installed power increase at year j. |  |  | 100% | Total (must be 100%)
| 0.6914 | Natural Gas fuel price (USD/Therm) - GCV
| 0.6 | Utility's price of one litre of diesel
| 54% | Efficiency of Gas Turbine (% on NCV basis)
| 50% | Efficiency of reciprocating diesel engine
| 0.0005 | Variable Operation and Maintenance (USD/kWh)
PC | 24.2714 | is the price of a tonne of CO2 in the first year
Instructions: enter appropriate values into the yellow shaded cells for the expected fixed load and variable load.
Fixed Load component |  |  | Variable Load component |  |  | Combined Loading (one year)
20% | Percent fixed load, not varying |  | 100 | Mid point (days)
100% | Percent of the year (365 days = 1 year) |  | 0.03 | Slope

## (1)
A-factor Calculation
On this sheet, users can calculate their A-factor using either equation A.2 or A.3 from IEC TS 60076-20. Equation A.2 is the more precise method, whereas A.3 is an approximation.
where: | [6 empty] | where:
O0j is the operating time of the transformer at year j in h; | [6 empty] | Cn/2 is the evaluation of the energy at mid-life of the transformer in cost per kWh if losses are expressed in kW;
Cj is the valorisation of the energy at year j in cost per KWh as losses are expressed in kW in the TCO formula; | [6 empty] | i is the discount rate fixed over the whole life of transformer (n years);
ij is the real discount rate at year j in per unit; | [6 empty] | n is the useful economic life of the transformer in years, which in the past has been close to the transformer's physical life expectancy (30 to 50 years).
n is the life expectancy of the transformer in years. | [6 empty] | IEC note: Use of Cn/2 is an approximation and overvalues the losses somewhat, but in the context of other uncertainties is acceptable.
Note: orange shaded cells are linked to Inputs tab. Cj (valorisation of energy in year j) is calculated on the next tab. A factor results are presented in cells D24 using Equation A.2 and D26 using A.3.
Inputs: |  | No CO2 Price | With CO2 Price
| O0j | 8760 | 8760 | the operating time of the transformer at year j in hours
| Cj | 0.041802 | 0.048169 | is the valorisation of the energy at year j in cost per kWh as losses are expressed in kilowatts in the TCO formula
| ij | 10% | 10% | is the real discount rate at year j in per unit
| n | 30 | 30 | is the life expectancy of the transformer in years
| iCj | 2% | 2% | growth rate of electricty prices in excess of inflation, to determine Cj in future years
|  |  | No CO2 Price | With CO2 Price
|  | A factor ($/kilowatt) | 4102.171 | 4726.9986 | using equation A.2
|  | A factor ($/kilowatt) | 4554.8485 | 5248.6262 | Estimated, using equation A.3
| No CO2 Price |  |  | With CO2 Price
Year | Energy Valorisation (Cj) | A ($/kW) for year j | Sum of A from 1 to j | Energy Valorisation (Cj) | A ($/kW) for year j | Sum of A from 1 to j
1 | 0.041802 | 332.8965 | 332.8965 | 0.048169 | 383.6021 | 383.6021
2 | 0.042638 | 308.6859 | 641.5824 | 0.049133 | 355.7038 | 739.3059
3 | 0.043491 | 286.236 | 927.8184 | 0.050115 | 329.8344 | 1069.1403
4 | 0.044361 | 265.4188 | 1193.2373 | 0.051118 | 305.8465 | 1374.9868
5 | 0.045248 | 246.1156 | 1439.3529 | 0.05214 | 283.6031 | 1658.5898
6 | 0.046153 | 228.2163 | 1667.5692 | 0.053183 | 262.9774 | 1921.5672
7 | 0.047076 | 211.6188 | 1879.188 | 0.054246 | 243.8518 | 2165.419
8 | 0.048017 | 196.2283 | 2075.4163 | 0.055331 | 226.1171 | 2391.5361
9 | 0.048978 | 181.9572 | 2257.3735 | 0.056438 | 209.6722 | 2601.2083
10 | 0.049957 | 168.7239 | 2426.0974 | 0.057567 | 194.4233 | 2795.6316
11 | 0.050956 | 156.4531 | 2582.5505 | 0.058718 | 180.2834 | 2975.9151
12 | 0.051976 | 145.0747 | 2727.6252 | 0.059892 | 167.1719 | 3143.087
13 | 0.053015 | 134.5238 | 2862.149 | 0.06109 | 155.014 | 3298.101
14 | 0.054075 | 124.7402 | 2986.8892 | 0.062312 | 143.7402 | 3441.8412
15 | 0.055157 | 115.6682 | 3102.5575 | 0.063558 | 133.2864 | 3575.1276
16 | 0.05626 | 107.256 | 3209.8135 | 0.064829 | 123.5928 | 3698.7204
17 | 0.057385 | 99.4556 | 3309.269 | 0.066126 | 114.6043 | 3813.3247
18 | 0.058533 | 92.2224 | 3401.4914 | 0.067449 | 106.2694 | 3919.5941
19 | 0.059704 | 85.5153 | 3487.0068 | 0.068798 | 98.5407 | 4018.1348
20 | 0.060898 | 79.296 | 3566.3028 | 0.070173 | 91.3741 | 4109.509
21 | 0.062116 | 73.5291 | 3639.8319 | 0.071577 | 84.7287 | 4194.2377
22 | 0.063358 | 68.1815 | 3708.0134 | 0.073008 | 78.5666 | 4272.8043
23 | 0.064625 | 63.2228 | 3771.2362 | 0.074469 | 72.8527 | 4345.657
24 | 0.065918 | 58.6248 | 3829.861 | 0.075958 | 67.5543 | 4413.2114
25 | 0.067236 | 54.3612 | 3884.2222 | 0.077477 | 62.6413 | 4475.8527
26 | 0.068581 | 50.4076 | 3934.6299 | 0.079027 | 58.0856 | 4533.9382
27 | 0.069952 | 46.7416 | 3981.3715 | 0.080607 | 53.8612 | 4587.7994
28 | 0.071351 | 43.3422 | 4024.7138 | 0.082219 | 49.944 | 4637.7433
29 | 0.072778 | 40.1901 | 4064.9038 | 0.083864 | 46.3117 | 4684.055
30 | 0.074234 | 37.2672 | 4102.171 | 0.085541 | 42.9436 | 4726.9986
31 | 0.075719 | 34.5568 | 4136.7278 | 0.087252 | 39.8204 | 4766.819
32 | 0.077233 | 32.0436 | 4168.7714 | 0.088997 | 36.9244 | 4803.7434
33 | 0.078778 | 29.7132 | 4198.4846 | 0.090777 | 34.239 | 4837.9823
34 | 0.080353 | 27.5522 | 4226.0368 | 0.092592 | 31.7489 | 4869.7312
35 | 0.08196 | 25.5484 | 4251.5852 | 0.094444 | 29.4398 | 4899.171
36 | 0.0836 | 23.6903 | 4275.2756 | 0.096333 | 27.2988 | 4926.4698
37 | 0.085272 | 21.9674 | 4297.243 | 0.09826 | 25.3134 | 4951.7832
38 | 0.086977 | 20.3698 | 4317.6127 | 0.10022 | 23.4724 | 4975.2556
39 | 0.088716 | 18.8883 | 4336.5011 | 0.10223 | 21.7653 | 4997.021
40 | 0.090491 | 17.5146 | 4354.0157 | 0.10427 | 20.1824 | 5017.2034
41 | 0.092301 | 16.2408 | 4370.2566 | 0.10636 | 18.7146 | 5035.918
42 | 0.094147 | 15.0597 | 4385.3163 | 0.10849 | 17.3535 | 5053.2715
43 | 0.09603 | 13.9644 | 4399.2807 | 0.11066 | 16.0915 | 5069.363
44 | 0.09795 | 12.9489 | 4412.2296 | 0.11287 | 14.9212 | 5084.2841
45 | 0.099909 | 12.0071 | 4424.2367 | 0.11513 | 13.836 | 5098.1201
46 | 0.10191 | 11.1339 | 4435.3706 | 0.11743 | 12.8297 | 5110.9499
47 | 0.10395 | 10.3241 | 4445.6947 | 0.11978 | 11.8967 | 5122.8465
48 | 0.10602 | 9.5733 | 4455.268 | 0.12217 | 11.0315 | 5133.878
49 | 0.10814 | 8.877 | 4464.145 | 0.12462 | 10.2292 | 5144.1072
50 | 0.11031 | 8.2314 | 4472.3765 | 0.12711 | 9.4852 | 5153.5924
51 | 0.11251 | 7.6328 | 4480.0093 | 0.12965 | 8.7954 | 5162.3878
52 | 0.11476 | 7.0777 | 4487.0869 | 0.13224 | 8.1557 | 5170.5435
53 | 0.11706 | 6.5629 | 4493.6499 | 0.13489 | 7.5626 | 5178.1061
54 | 0.1194 | 6.0856 | 4499.7355 | 0.13759 | 7.0126 | 5185.1187
55 | 0.12179 | 5.643 | 4505.3786 | 0.14034 | 6.5026 | 5191.6212
56 | 0.12422 | 5.2326 | 4510.6112 | 0.14315 | 6.0297 | 5197.6509
57 | 0.12671 | 4.8521 | 4515.4633 | 0.14601 | 5.5911 | 5203.242
58 | 0.12924 | 4.4992 | 4519.9625 | 0.14893 | 5.1845 | 5208.4266
59 | 0.13183 | 4.172 | 4524.1345 | 0.15191 | 4.8075 | 5213.234
60 | 0.13446 | 3.8686 | 4528.0031 | 0.15495 | 4.4578 | 5217.6918
61 | 0.13715 | 3.5872 | 4531.5903 | 0.15804 | 4.1336 | 5221.8254
62 | 0.1399 | 3.3263 | 4534.9166 | 0.16121 | 3.833 | 5225.6584
63 | 0.14269 | 3.0844 | 4538.0011 | 0.16443 | 3.5542 | 5229.2127
64 | 0.14555 | 2.8601 | 4540.8612 | 0.16772 | 3.2957 | 5232.5084
65 | 0.14846 | 2.6521 | 4543.5132 | 0.17107 | 3.056 | 5235.5645
66 | 0.15143 | 2.4592 | 4545.9725 | 0.17449 | 2.8338 | 5238.3982
67 | 0.15446 | 2.2804 | 4548.2528 | 0.17798 | 2.6277 | 5241.0259
68 | 0.15755 | 2.1145 | 4550.3673 | 0.18154 | 2.4366 | 5243.4625
69 | 0.1607 | 1.9607 | 4552.3281 | 0.18517 | 2.2594 | 5245.7219
70 | 0.16391 | 1.8181 | 4554.1462 | 0.18888 | 2.0951 | 5247.817
71 | 0.16719 | 1.6859 | 4555.8321 | 0.19266 | 1.9427 | 5249.7597
72 | 0.17053 | 1.5633 | 4557.3954 | 0.19651 | 1.8014 | 5251.5611
73 | 0.17394 | 1.4496 | 4558.845 | 0.20044 | 1.6704 | 5253.2315
74 | 0.17742 | 1.3442 | 4560.1892 | 0.20445 | 1.5489 | 5254.7804
75 | 0.18097 | 1.2464 | 4561.4356 | 0.20854 | 1.4363 | 5256.2167
76 | 0.18459 | 1.1558 | 4562.5914 | 0.21271 | 1.3318 | 5257.5485
77 | 0.18828 | 1.0717 | 4563.6631 | 0.21696 | 1.235 | 5258.7834
78 | 0.19205 | 0.99377 | 4564.6568 | 0.2213 | 1.1451 | 5259.9286
79 | 0.19589 | 0.9215 | 4565.5783 | 0.22573 | 1.0619 | 5260.9904
80 | 0.19981 | 0.85448 | 4566.4328 | 0.23024 | 0.98463 | 5261.975
81 | 0.2038 | 0.79233 | 4567.2251 | 0.23485 | 0.91302 | 5262.8881
82 | 0.20788 | 0.73471 | 4567.9599 | 0.23954 | 0.84662 | 5263.7347
83 | 0.21204 | 0.68128 | 4568.6411 | 0.24433 | 0.78505 | 5264.5197
84 | 0.21628 | 0.63173 | 4569.2729 | 0.24922 | 0.72795 | 5265.2477
85 | 0.2206 | 0.58578 | 4569.8586 | 0.2542 | 0.67501 | 5265.9227
86 | 0.22502 | 0.54318 | 4570.4018 | 0.25929 | 0.62592 | 5266.5486
87 | 0.22952 | 0.50368 | 4570.9055 | 0.26447 | 0.5804 | 5267.129
88 | 0.23411 | 0.46705 | 4571.3726 | 0.26976 | 0.53819 | 5267.6672
89 | 0.23879 | 0.43308 | 4571.8056 | 0.27516 | 0.49905 | 5268.1662
90 | 0.24356 | 0.40158 | 4572.2072 | 0.28066 | 0.46275 | 5268.629
91 | 0.24844 | 0.37238 | 4572.5796 | 0.28628 | 0.4291 | 5269.0581
92 | 0.2534 | 0.3453 | 4572.9249 | 0.292 | 0.39789 | 5269.456
93 | 0.25847 | 0.32018 | 4573.2451 | 0.29784 | 0.36895 | 5269.8249
94 | 0.26364 | 0.2969 | 4573.542 | 0.3038 | 0.34212 | 5270.167
95 | 0.26891 | 0.2753 | 4573.8173 | 0.30987 | 0.31724 | 5270.4843
96 | 0.27429 | 0.25528 | 4574.0726 | 0.31607 | 0.29417 | 5270.7784
97 | 0.27978 | 0.23672 | 4574.3093 | 0.32239 | 0.27277 | 5271.0512
98 | 0.28537 | 0.2195 | 4574.5288 | 0.32884 | 0.25293 | 5271.3042
99 | 0.29108 | 0.20354 | 4574.7323 | 0.33542 | 0.23454 | 5271.5387

## (2)
Cj is the valorisation of the energy at year j in cost per Wh if losses are expressed in W
|  | No CO2 Price | With CO2 Price
| Cj | 0.041802 | 0.048169 | is the valorisation of the energy at year j in cost per kWh because losses are expressed in kilowatts in the TCO formula
Note: orange shaded cells are linked to Inputs tab.
| Your Percentage Mix | No CO2 Price | With CO2 Price | Indicative Cost* | Description
|  | ($/MWh) | ($/MWh) | ($/MWh)
| 10% | 0.5 | 0.5 | 0.5 | Solar - Photovoltaic (O&M US$0.0005/kWh)
| 20% | 0.5 | 0.5 | 0.5 | Hydroelectric power (O&M US$0.0005/kWh)
| 5% | 0.5 | 0.5 | 0.5 | Wind Turbine (O&M US$0.0005/kWh)
| 50% | 49.0016 | 58.0256 | 50 | Natural Gas - Peaking capacity
| 15% | 114.1751 | 126.5429 | 120 | Diesel Generator
| 0% | 0 | 0 | 0
Total: | 100% | 41.8021 | 48.1692 | USD/MWh
*Note: the renewable sources are set low because the marginal cost of generation is close to zero, so this just reflects a small maintenance charge. The Natural Gas value should be based on the cost of gas plant, so marginal cost is the cost of gas divided by the efficiency of conversion of the plant. So for example, if the gas turbine was say 35% efficient and the utility's fuel price for natural gas was $20/MWh fuel, then the marginal cost would be US$20/0.35 = US$57.14 / MWh electricity.
Calculator to determine Natural Gas Marginal Cost of a MWh of Electricity
| 0.6914 | Natural Gas fuel price (USD/Therm) - GCV
| 1.11 | GCV, Gross calorific value of fuel, Kcal/Kg. NCV, Net Calorific Value of fuel, Kcal/Kg
| 0.10548 | 1 GJ / Therm |  |  |  | Natural Gas CO2 Emissions Charge Calculation
| 7.2758 | Energy price USD/GJ (NCV) |  |  |  | 5.3 | kg CO2 per therm
| 54% | Efficiency (% on NCV basis) |  |  |  | 14.2552 | kWh/therm
| 0.048502 | Fuel cost (USD/kWh) |  |  |  | 0.37179 | Kg/kWh
| 0.0005 | Variable Operation and Maintenance (US cents/kWh) |  |  |  | 24.2714 | USD/tonne CO2
| 0.009024 | Charge for CO2 Emissions (USD/kWh) |  |  |  | 0.009024 | USD/kWh
| 49.0016 | Energy cost without CO2 Cost (US dollars/MWh)
| 58.0256 | Energy cost with CO2 Cost (US dollars/MWh)
Calculator to determine Diesel Marginal Cost of a MWh of Electricity
| 0.6 | Utility's price of one litre of diesel |  |  |  | Diesel CO2 Emissions Charge Calculation
| 38 | MJ per litre of diesel |  |  |  | 10.18 | kg of CO2/gallon of diesel
| 15.7895 | Energy price USD/GJ (NCV) |  |  |  | 3.785 | litres / US gallon
| 50% | Efficiency of reciprocating diesel engine |  |  |  | 2.6896 | kg of CO2/litre
| 0.11368 | Fuel cost (USD/kWh) |  |  |  | 5.2782 | kWh/litre
| 0.0005 | Variable Operation and Maintenance (USD/kWh) |  |  |  | 0.50956 | Kg/kWh
| 0.012368 | Charge for CO2 Emissions (USD/kWh) |  |  |  | 24.2714 | USD/tonne CO2
| 114.1751 | Energy cost without CO2 Cost (US dollars/MWh) |  |  |  | 0.012368 | USD/kWh
| 126.5429 | Energy cost with CO2 Cost (US dollars/MWh)
On this sheet, the calculator determines the utility's valorisation of energy, which is a very important input to the loss evaluation metrics. The valorisation of energy is the marginal cost of a kWh (not an average cost). Thus it reflects the generation cost (e.g. fuel) for producing electricity during peak times, such as from a hydro facility or a natural gas turbine, both of which are generating assets that can be adjusted up and down as required to follow load. Coal and Nuclear power plants are not included in the table as these are typically base-load units and do not follow load. Marginal cost of renewable resources are close to zero, whereas the marginal cost of natural gas supplied kWh will vary with the efficiency of the system.

## (3)
B-factor Calculation
On this sheet, users can calculate their B-factor using either equation A.5 or A.7 from IEC TS 60076-20. Equation A.5 is the more precise method, whereas A.7 is an approximation.
Note: orange shaded cells are linked to Inputs tab.
Inputs:
| μ | 0.25038 | is the average load loss factor as defined in Equation (A.4)
| Cj | 0.041802 | is the total cost of the energy at year j in cost per kWh as losses are expressed in kilowatts; no CO2 price
| Cj | 0.048169 | is the total cost of the energy at year j in cost per kWh as losses are expressed in kilowatts; including CO2 price
| ij | 10% | is the real discount rate at year j in per unit; generally the weighted average cost of capital, provided by the regulator
| Oaj | 2000 | is the operating time of the transformer at variable load during year j in h;
| Ofj | 8760 | is the operating time of the transformer at fixed load during year j in h, usually 8 760 h if the transformer is operated all year round;
| Taj | 0.5 | is the share of variable load in the total load loss factor at year j;
| Tfj | 0.5 | is the share of fixed load in the total load loss factor at year j; |  |  |  | Taj + Tfj = 1
| n | 30 | is the life expectancy of the transformer in years;
| Cμj | 0 | is the rate of load loss factor increase at year j;
| Caj | 0 | is the rate of installed power increase at year j.
|  | No CO2 Price | With CO2 Price
| B factor ($/kilowatt) | 1535.6767 | 1769.5853 | using equation A.5
| B factor ($/kilowatt) | 2015.758 | 2322.7908 | Estimated, using equation A.7
| No CO2 Price |  |  | With CO2 Price
Year | Valorisation | Term | B value | Valorisation | Term | B value
1 | 0.041802 | 51.1892 | 51.1892 | 0.048169 | 58.9862 | 58.9862
2 | 0.045982 | 51.1892 | 102.3784 | 0.052986 | 58.9862 | 117.9724
3 | 0.050581 | 51.1892 | 153.5677 | 0.058285 | 58.9862 | 176.9585
4 | 0.055639 | 51.1892 | 204.7569 | 0.064113 | 58.9862 | 235.9447
5 | 0.061202 | 51.1892 | 255.9461 | 0.070525 | 58.9862 | 294.9309
6 | 0.067323 | 51.1892 | 307.1353 | 0.077577 | 58.9862 | 353.9171
7 | 0.074055 | 51.1892 | 358.3246 | 0.085335 | 58.9862 | 412.9032
8 | 0.08146 | 51.1892 | 409.5138 | 0.093868 | 58.9862 | 471.8894
9 | 0.089606 | 51.1892 | 460.703 | 0.10325 | 58.9862 | 530.8756
10 | 0.098567 | 51.1892 | 511.8922 | 0.11358 | 58.9862 | 589.8618
11 | 0.10842 | 51.1892 | 563.0815 | 0.12494 | 58.9862 | 648.848
12 | 0.11927 | 51.1892 | 614.2707 | 0.13743 | 58.9862 | 707.8341
13 | 0.13119 | 51.1892 | 665.4599 | 0.15118 | 58.9862 | 766.8203
14 | 0.14431 | 51.1892 | 716.6491 | 0.16629 | 58.9862 | 825.8065
15 | 0.15874 | 51.1892 | 767.8384 | 0.18292 | 58.9862 | 884.7927
16 | 0.17462 | 51.1892 | 819.0276 | 0.20121 | 58.9862 | 943.7788
17 | 0.19208 | 51.1892 | 870.2168 | 0.22134 | 58.9862 | 1002.765
18 | 0.21129 | 51.1892 | 921.406 | 0.24347 | 58.9862 | 1061.7512
19 | 0.23242 | 51.1892 | 972.5952 | 0.26782 | 58.9862 | 1120.7374
20 | 0.25566 | 51.1892 | 1023.7845 | 0.2946 | 58.9862 | 1179.7236
21 | 0.28122 | 51.1892 | 1074.9737 | 0.32406 | 58.9862 | 1238.7097
22 | 0.30935 | 51.1892 | 1126.1629 | 0.35646 | 58.9862 | 1297.6959
23 | 0.34028 | 51.1892 | 1177.3521 | 0.39211 | 58.9862 | 1356.6821
24 | 0.37431 | 51.1892 | 1228.5414 | 0.43132 | 58.9862 | 1415.6683
25 | 0.41174 | 51.1892 | 1279.7306 | 0.47445 | 58.9862 | 1474.6544
26 | 0.45291 | 51.1892 | 1330.9198 | 0.5219 | 58.9862 | 1533.6406
27 | 0.4982 | 51.1892 | 1382.109 | 0.57409 | 58.9862 | 1592.6268
28 | 0.54802 | 51.1892 | 1433.2983 | 0.6315 | 58.9862 | 1651.613
29 | 0.60283 | 51.1892 | 1484.4875 | 0.69465 | 58.9862 | 1710.5991
30 | 0.66311 | 51.1892 | 1535.6767 | 0.76411 | 58.9862 | 1769.5853
31 | 0.72942 | 51.1892 | 1586.8659 | 0.84052 | 58.9862 | 1828.5715
32 | 0.80236 | 51.1892 | 1638.0552 | 0.92458 | 58.9862 | 1887.5577
33 | 0.8826 | 51.1892 | 1689.2444 | 1.017 | 58.9862 | 1946.5439
34 | 0.97086 | 51.1892 | 1740.4336 | 1.1187 | 58.9862 | 2005.53
35 | 1.0679 | 51.1892 | 1791.6228 | 1.2306 | 58.9862 | 2064.5162
36 | 1.1747 | 51.1892 | 1842.812 | 1.3537 | 58.9862 | 2123.5024
37 | 1.2922 | 51.1892 | 1894.0013 | 1.489 | 58.9862 | 2182.4886
38 | 1.4214 | 51.1892 | 1945.1905 | 1.6379 | 58.9862 | 2241.4747
39 | 1.5636 | 51.1892 | 1996.3797 | 1.8017 | 58.9862 | 2300.4609
40 | 1.7199 | 51.1892 | 2047.5689 | 1.9819 | 58.9862 | 2359.4471
41 | 1.8919 | 51.1892 | 2098.7582 | 2.1801 | 58.9862 | 2418.4333
42 | 2.0811 | 51.1892 | 2149.9474 | 2.3981 | 58.9862 | 2477.4195
43 | 2.2892 | 51.1892 | 2201.1366 | 2.6379 | 58.9862 | 2536.4056
44 | 2.5182 | 51.1892 | 2252.3258 | 2.9017 | 58.9862 | 2595.3918
45 | 2.77 | 51.1892 | 2303.5151 | 3.1919 | 58.9862 | 2654.378
46 | 3.047 | 51.1892 | 2354.7043 | 3.5111 | 58.9862 | 2713.3642
47 | 3.3517 | 51.1892 | 2405.8935 | 3.8622 | 58.9862 | 2772.3503
48 | 3.6868 | 51.1892 | 2457.0827 | 4.2484 | 58.9862 | 2831.3365
49 | 4.0555 | 51.1892 | 2508.272 | 4.6732 | 58.9862 | 2890.3227
50 | 4.4611 | 51.1892 | 2559.4612 | 5.1406 | 58.9862 | 2949.3089
51 | 4.9072 | 51.1892 | 2610.6504 | 5.6546 | 58.9862 | 3008.2951
52 | 5.3979 | 51.1892 | 2661.8396 | 6.2201 | 58.9862 | 3067.2812
53 | 5.9377 | 51.1892 | 2713.0288 | 6.8421 | 58.9862 | 3126.2674
54 | 6.5315 | 51.1892 | 2764.2181 | 7.5263 | 58.9862 | 3185.2536
55 | 7.1846 | 51.1892 | 2815.4073 | 8.2789 | 58.9862 | 3244.2398
56 | 7.9031 | 51.1892 | 2866.5965 | 9.1068 | 58.9862 | 3303.2259
57 | 8.6934 | 51.1892 | 2917.7857 | 10.0175 | 58.9862 | 3362.2121
58 | 9.5627 | 51.1892 | 2968.975 | 11.0193 | 58.9862 | 3421.1983
59 | 10.519 | 51.1892 | 3020.1642 | 12.1212 | 58.9862 | 3480.1845
60 | 11.5709 | 51.1892 | 3071.3534 | 13.3333 | 58.9862 | 3539.1707
61 | 12.728 | 51.1892 | 3122.5426 | 14.6666 | 58.9862 | 3598.1568
62 | 14.0008 | 51.1892 | 3173.7319 | 16.1333 | 58.9862 | 3657.143
63 | 15.4008 | 51.1892 | 3224.9211 | 17.7466 | 58.9862 | 3716.1292
64 | 16.9409 | 51.1892 | 3276.1103 | 19.5213 | 58.9862 | 3775.1154
65 | 18.635 | 51.1892 | 3327.2995 | 21.4734 | 58.9862 | 3834.1015
66 | 20.4985 | 51.1892 | 3378.4887 | 23.6208 | 58.9862 | 3893.0877
67 | 22.5484 | 51.1892 | 3429.678 | 25.9829 | 58.9862 | 3952.0739
68 | 24.8032 | 51.1892 | 3480.8672 | 28.5811 | 58.9862 | 4011.0601
69 | 27.2835 | 51.1892 | 3532.0564 | 31.4392 | 58.9862 | 4070.0462
70 | 30.0119 | 51.1892 | 3583.2456 | 34.5832 | 58.9862 | 4129.0324
71 | 33.0131 | 51.1892 | 3634.4349 | 38.0415 | 58.9862 | 4188.0186
72 | 36.3144 | 51.1892 | 3685.6241 | 41.8456 | 58.9862 | 4247.0048
73 | 39.9458 | 51.1892 | 3736.8133 | 46.0302 | 58.9862 | 4305.991
74 | 43.9404 | 51.1892 | 3788.0025 | 50.6332 | 58.9862 | 4364.9771
75 | 48.3344 | 51.1892 | 3839.1918 | 55.6965 | 58.9862 | 4423.9633
76 | 53.1679 | 51.1892 | 3890.381 | 61.2662 | 58.9862 | 4482.9495
77 | 58.4847 | 51.1892 | 3941.5702 | 67.3928 | 58.9862 | 4541.9357
78 | 64.3331 | 51.1892 | 3992.7594 | 74.1321 | 58.9862 | 4600.9218
79 | 70.7664 | 51.1892 | 4043.9487 | 81.5453 | 58.9862 | 4659.908
80 | 77.8431 | 51.1892 | 4095.1379 | 89.6998 | 58.9862 | 4718.8942
81 | 85.6274 | 51.1892 | 4146.3271 | 98.6698 | 58.9862 | 4777.8804
82 | 94.1901 | 51.1892 | 4197.5163 | 108.5368 | 58.9862 | 4836.8666
83 | 103.6091 | 51.1892 | 4248.7055 | 119.3905 | 58.9862 | 4895.8527
84 | 113.97 | 51.1892 | 4299.8948 | 131.3295 | 58.9862 | 4954.8389
85 | 125.3671 | 51.1892 | 4351.084 | 144.4625 | 58.9862 | 5013.8251
86 | 137.9038 | 51.1892 | 4402.2732 | 158.9087 | 58.9862 | 5072.8113
87 | 151.6941 | 51.1892 | 4453.4624 | 174.7996 | 58.9862 | 5131.7974
88 | 166.8635 | 51.1892 | 4504.6517 | 192.2796 | 58.9862 | 5190.7836
89 | 183.5499 | 51.1892 | 4555.8409 | 211.5075 | 58.9862 | 5249.7698
90 | 201.9049 | 51.1892 | 4607.0301 | 232.6583 | 58.9862 | 5308.756
91 | 222.0954 | 51.1892 | 4658.2193 | 255.9241 | 58.9862 | 5367.7422
92 | 244.3049 | 51.1892 | 4709.4086 | 281.5165 | 58.9862 | 5426.7283
93 | 268.7354 | 51.1892 | 4760.5978 | 309.6682 | 58.9862 | 5485.7145
94 | 295.6089 | 51.1892 | 4811.787 | 340.635 | 58.9862 | 5544.7007
95 | 325.1698 | 51.1892 | 4862.9762 | 374.6985 | 58.9862 | 5603.6869
96 | 357.6868 | 51.1892 | 4914.1655 | 412.1684 | 58.9862 | 5662.673
97 | 393.4555 | 51.1892 | 4965.3547 | 453.3852 | 58.9862 | 5721.6592
98 | 432.8011 | 51.1892 | 5016.5439 | 498.7237 | 58.9862 | 5780.6454
99 | 476.0812 | 51.1892 | 5067.7331 | 548.5961 | 58.9862 | 5839.6316
Note: Set equal to Cμj; Usually Cμj and Caj are taken equal to zero which corresponds to a situation where the investment is assessed on the basis that the average loading of transformer as invariant. If this is not the case special care shall be taken to avoid overloading of transformer from a certain year, as if Cμj is greater than Caj the final factor is greater than one.

## (4)
Load Loss Factor Calculation
On this sheet, users estimate the load that the transformer will experience during a typical year
Average Load Loss Factor (μ)
the square of the RMS value of the instantaneous load factors by:
where
T is equivalent to one year; if k(t) is defined per h T is 8 760 h; if k(t) is defined per minutes T is 525 600 min;
k(t) is the load factor as a function of time.
Note: orange shaded cells are linked to Inputs tab.
| Fixed Load component | [5 empty] | Variable Load component |  | Combined Loading (one year)
| 20% | Percent fixed load, not varying |  |  |  |  | 100 | Mid point (days)
| 100% | Percent of the year (365 days = 1 year) |  |  |  |  | 0.03 | Slope
| Fixed Share | Variable Share | Total (year)
RMS: | 0.2 | 0.34887 | 0.50037 |  | 0.25038 | Calculated Value used in B-factor calculation
Days | Fixed | Variable | Total | k(t)^2 | Sum
1 | 20% | 76.1% | 96.1% | 0.92344 | 0.92344
2 | 20% | 75.98% | 95.98% | 0.92128 | 1.8447
3 | 20% | 75.87% | 95.87% | 0.91905 | 2.7638
4 | 20% | 75.75% | 95.75% | 0.91677 | 3.6805
5 | 20% | 75.63% | 95.63% | 0.91442 | 4.595
6 | 20% | 75.5% | 95.5% | 0.91202 | 5.507
7 | 20% | 75.37% | 95.37% | 0.90956 | 6.4165
8 | 20% | 75.24% | 95.24% | 0.90703 | 7.3236
9 | 20% | 75.1% | 95.1% | 0.90444 | 8.228
10 | 20% | 74.96% | 94.96% | 0.90178 | 9.1298
11 | 20% | 74.82% | 94.82% | 0.89906 | 10.0288
12 | 20% | 74.67% | 94.67% | 0.89627 | 10.9251
13 | 20% | 74.52% | 94.52% | 0.89341 | 11.8185
14 | 20% | 74.37% | 94.37% | 0.89048 | 12.709
15 | 20% | 74.21% | 94.21% | 0.88747 | 13.5965
16 | 20% | 74.04% | 94.04% | 0.8844 | 14.4809
17 | 20% | 73.88% | 93.88% | 0.88125 | 15.3621
18 | 20% | 73.7% | 93.7% | 0.87803 | 16.2401
19 | 20% | 73.53% | 93.53% | 0.87473 | 17.1149
20 | 20% | 73.35% | 93.35% | 0.87135 | 17.9862
21 | 20% | 73.16% | 93.16% | 0.86789 | 18.8541
22 | 20% | 72.97% | 92.97% | 0.86436 | 19.7185
23 | 20% | 72.78% | 92.78% | 0.86074 | 20.5792
24 | 20% | 72.58% | 92.58% | 0.85704 | 21.4363
25 | 20% | 72.37% | 92.37% | 0.85326 | 22.2895
26 | 20% | 72.16% | 92.16% | 0.84939 | 23.1389
27 | 20% | 71.95% | 91.95% | 0.84544 | 23.9844
28 | 20% | 71.73% | 91.73% | 0.8414 | 24.8258
29 | 20% | 71.5% | 91.5% | 0.83728 | 25.663
30 | 20% | 71.27% | 91.27% | 0.83306 | 26.4961
31 | 20% | 71.04% | 91.04% | 0.82876 | 27.3249
32 | 20% | 70.79% | 90.79% | 0.82437 | 28.1492
33 | 20% | 70.55% | 90.55% | 0.81988 | 28.9691
34 | 20% | 70.29% | 90.29% | 0.81531 | 29.7844
35 | 20% | 70.04% | 90.04% | 0.81064 | 30.5951
36 | 20% | 69.77% | 89.77% | 0.80588 | 31.4009
37 | 20% | 69.5% | 89.5% | 0.80103 | 32.202
38 | 20% | 69.22% | 89.22% | 0.79609 | 32.9981
39 | 20% | 68.94% | 88.94% | 0.79105 | 33.7891
40 | 20% | 68.65% | 88.65% | 0.78592 | 34.575
41 | 20% | 68.36% | 88.36% | 0.78069 | 35.3557
42 | 20% | 68.05% | 88.05% | 0.77537 | 36.1311
43 | 20% | 67.75% | 87.75% | 0.76995 | 36.901
44 | 20% | 67.43% | 87.43% | 0.76444 | 37.6655
45 | 20% | 67.11% | 87.11% | 0.75884 | 38.4243
46 | 20% | 66.78% | 86.78% | 0.75314 | 39.1775
47 | 20% | 66.45% | 86.45% | 0.74735 | 39.9248
48 | 20% | 66.11% | 86.11% | 0.74146 | 40.6663
49 | 20% | 65.76% | 85.76% | 0.73549 | 41.4018
50 | 20% | 65.41% | 85.41% | 0.72942 | 42.1312
51 | 20% | 65.04% | 85.04% | 0.72326 | 42.8544
52 | 20% | 64.68% | 84.68% | 0.71701 | 43.5714
53 | 20% | 64.3% | 84.3% | 0.71067 | 44.2821
54 | 20% | 63.92% | 83.92% | 0.70424 | 44.9864
55 | 20% | 63.53% | 83.53% | 0.69773 | 45.6841
56 | 20% | 63.13% | 83.13% | 0.69114 | 46.3752
57 | 20% | 62.73% | 82.73% | 0.68445 | 47.0597
58 | 20% | 62.32% | 82.32% | 0.67769 | 47.7374
59 | 20% | 61.91% | 81.91% | 0.67085 | 48.4082
60 | 20% | 61.48% | 81.48% | 0.66393 | 49.0722
61 | 20% | 61.05% | 81.05% | 0.65694 | 49.7291
62 | 20% | 60.61% | 80.61% | 0.64987 | 50.379
63 | 20% | 60.17% | 80.17% | 0.64273 | 51.0217
64 | 20% | 59.72% | 79.72% | 0.63552 | 51.6572
65 | 20% | 59.26% | 79.26% | 0.62825 | 52.2854
66 | 20% | 58.8% | 78.8% | 0.62091 | 52.9064
67 | 20% | 58.33% | 78.33% | 0.61351 | 53.5199
68 | 20% | 57.85% | 77.85% | 0.60606 | 54.1259
69 | 20% | 57.37% | 77.37% | 0.59855 | 54.7245
70 | 20% | 56.88% | 76.88% | 0.59099 | 55.3155
71 | 20% | 56.38% | 76.38% | 0.58339 | 55.8989
72 | 20% | 55.88% | 75.88% | 0.57574 | 56.4746
73 | 20% | 55.37% | 75.37% | 0.56805 | 57.0426
74 | 20% | 54.85% | 74.85% | 0.56032 | 57.603
75 | 20% | 54.33% | 74.33% | 0.55256 | 58.1555
76 | 20% | 53.81% | 73.81% | 0.54477 | 58.7003
77 | 20% | 53.28% | 73.28% | 0.53696 | 59.2372
78 | 20% | 52.74% | 72.74% | 0.52912 | 59.7664
79 | 20% | 52.2% | 72.2% | 0.52127 | 60.2876
80 | 20% | 51.65% | 71.65% | 0.51341 | 60.801
81 | 20% | 51.1% | 71.1% | 0.50554 | 61.3066
82 | 20% | 50.54% | 70.54% | 0.49766 | 61.8042
83 | 20% | 49.98% | 69.98% | 0.48978 | 62.294
84 | 20% | 49.42% | 69.42% | 0.48191 | 62.7759
85 | 20% | 48.85% | 68.85% | 0.47405 | 63.25
86 | 20% | 48.28% | 68.28% | 0.4662 | 63.7162
87 | 20% | 47.7% | 67.7% | 0.45836 | 64.1745
88 | 20% | 47.12% | 67.12% | 0.45055 | 64.6251
89 | 20% | 46.54% | 66.54% | 0.44277 | 65.0679
90 | 20% | 45.96% | 65.96% | 0.43501 | 65.5029
91 | 20% | 45.37% | 65.37% | 0.42729 | 65.9302
92 | 20% | 44.78% | 64.78% | 0.41961 | 66.3498
93 | 20% | 44.18% | 64.18% | 0.41197 | 66.7617
94 | 20% | 43.59% | 63.59% | 0.40437 | 67.1661
95 | 20% | 42.99% | 62.99% | 0.39683 | 67.5629
96 | 20% | 42.4% | 62.4% | 0.38934 | 67.9523
97 | 20% | 41.8% | 61.8% | 0.38191 | 68.3342
98 | 20% | 41.2% | 61.2% | 0.37454 | 68.7087
99 | 20% | 40.6% | 60.6% | 0.36724 | 69.076
100 | 20% | 40% | 60% | 0.36 | 69.436
101 | 20% | 39.4% | 59.4% | 0.35284 | 69.7888
102 | 20% | 38.8% | 58.8% | 0.34575 | 70.1346
103 | 20% | 38.2% | 58.2% | 0.33874 | 70.4733
104 | 20% | 37.6% | 57.6% | 0.33181 | 70.8051
105 | 20% | 37.01% | 57.01% | 0.32496 | 71.1301
106 | 20% | 36.41% | 56.41% | 0.31821 | 71.4483
107 | 20% | 35.82% | 55.82% | 0.31154 | 71.7598
108 | 20% | 35.22% | 55.22% | 0.30496 | 72.0648
109 | 20% | 34.63% | 54.63% | 0.29847 | 72.3632
110 | 20% | 34.04% | 54.04% | 0.29208 | 72.6553
111 | 20% | 33.46% | 53.46% | 0.28579 | 72.9411
112 | 20% | 32.88% | 52.88% | 0.2796 | 73.2207
113 | 20% | 32.3% | 52.3% | 0.2735 | 73.4942
114 | 20% | 31.72% | 51.72% | 0.26751 | 73.7617
115 | 20% | 31.15% | 51.15% | 0.26162 | 74.0233
116 | 20% | 30.58% | 50.58% | 0.25584 | 74.2792
117 | 20% | 30.02% | 50.02% | 0.25015 | 74.5293
118 | 20% | 29.46% | 49.46% | 0.24458 | 74.7739
119 | 20% | 28.9% | 48.9% | 0.23911 | 75.013
120 | 20% | 28.35% | 48.35% | 0.23375 | 75.2468
121 | 20% | 27.8% | 47.8% | 0.22849 | 75.4753
122 | 20% | 27.26% | 47.26% | 0.22334 | 75.6986
123 | 20% | 26.72% | 46.72% | 0.2183 | 75.9169
124 | 20% | 26.19% | 46.19% | 0.21336 | 76.1303
125 | 20% | 25.67% | 45.67% | 0.20854 | 76.3388
126 | 20% | 25.15% | 45.15% | 0.20381 | 76.5426
127 | 20% | 24.63% | 44.63% | 0.19919 | 76.7418
128 | 20% | 24.12% | 44.12% | 0.19468 | 76.9365
129 | 20% | 23.62% | 43.62% | 0.19027 | 77.1268
130 | 20% | 23.12% | 43.12% | 0.18597 | 77.3127
131 | 20% | 22.63% | 42.63% | 0.18177 | 77.4945
132 | 20% | 22.15% | 42.15% | 0.17766 | 77.6722
133 | 20% | 21.67% | 41.67% | 0.17366 | 77.8458
134 | 20% | 21.2% | 41.2% | 0.16976 | 78.0156
135 | 20% | 20.74% | 40.74% | 0.16596 | 78.1815
136 | 20% | 20.28% | 40.28% | 0.16225 | 78.3438
137 | 20% | 19.83% | 39.83% | 0.15864 | 78.5024
138 | 20% | 19.39% | 39.39% | 0.15512 | 78.6576
139 | 20% | 18.95% | 38.95% | 0.1517 | 78.8093
140 | 20% | 18.52% | 38.52% | 0.14836 | 78.9576
141 | 20% | 18.09% | 38.09% | 0.14512 | 79.1027
142 | 20% | 17.68% | 37.68% | 0.14196 | 79.2447
143 | 20% | 17.27% | 37.27% | 0.13889 | 79.3836
144 | 20% | 16.87% | 36.87% | 0.13591 | 79.5195
145 | 20% | 16.47% | 36.47% | 0.133 | 79.6525
146 | 20% | 16.08% | 36.08% | 0.13018 | 79.7827
147 | 20% | 15.7% | 35.7% | 0.12744 | 79.9101
148 | 20% | 15.32% | 35.32% | 0.12478 | 80.0349
149 | 20% | 14.96% | 34.96% | 0.12219 | 80.1571
150 | 20% | 14.59% | 34.59% | 0.11967 | 80.2768
151 | 20% | 14.24% | 34.24% | 0.11723 | 80.394
152 | 20% | 13.89% | 33.89% | 0.11486 | 80.5089
153 | 20% | 13.55% | 33.55% | 0.11257 | 80.6214
154 | 20% | 13.22% | 33.22% | 0.11033 | 80.7318
155 | 20% | 12.89% | 32.89% | 0.10817 | 80.8399
156 | 20% | 12.57% | 32.57% | 0.10607 | 80.946
157 | 20% | 12.25% | 32.25% | 0.10403 | 81.05
158 | 20% | 11.95% | 31.95% | 0.10205 | 81.1521
159 | 20% | 11.64% | 31.64% | 0.10013 | 81.2522
160 | 20% | 11.35% | 31.35% | 0.09827 | 81.3505
161 | 20% | 11.06% | 31.06% | 0.096467 | 81.4469
162 | 20% | 10.78% | 30.78% | 0.094718 | 81.5416
163 | 20% | 10.5% | 30.5% | 0.093022 | 81.6347
164 | 20% | 10.23% | 30.23% | 0.091379 | 81.726
165 | 20% | 9.964% | 29.96% | 0.089786 | 81.8158
166 | 20% | 9.706% | 29.71% | 0.088242 | 81.9041
167 | 20% | 9.453% | 29.45% | 0.086745 | 81.9908
168 | 20% | 9.205% | 29.21% | 0.085295 | 82.0761
169 | 20% | 8.964% | 28.96% | 0.08389 | 82.16
170 | 20% | 8.728% | 28.73% | 0.082528 | 82.2425
171 | 20% | 8.497% | 28.5% | 0.081209 | 82.3237
172 | 20% | 8.272% | 28.27% | 0.079931 | 82.4037
173 | 20% | 8.052% | 28.05% | 0.078692 | 82.4824
174 | 20% | 7.838% | 27.84% | 0.077493 | 82.5599
175 | 20% | 7.628% | 27.63% | 0.07633 | 82.6362
176 | 20% | 7.423% | 27.42% | 0.075204 | 82.7114
177 | 20% | 7.224% | 27.22% | 0.074114 | 82.7855
178 | 20% | 7.029% | 27.03% | 0.073057 | 82.8586
179 | 20% | 6.839% | 26.84% | 0.072034 | 82.9306
180 | 20% | 6.654% | 26.65% | 0.071043 | 83.0016
181 | 20% | 6.473% | 26.47% | 0.070082 | 83.0717
182 | 20% | 6.297% | 26.3% | 0.069152 | 83.1409
183 | 20% | 6.125% | 26.12% | 0.068251 | 83.2091
184 | 20% | 5.957% | 25.96% | 0.067379 | 83.2765
185 | 20% | 5.794% | 25.79% | 0.066534 | 83.343
186 | 20% | 5.635% | 25.63% | 0.065715 | 83.4088
187 | 20% | 5.48% | 25.48% | 0.064922 | 83.4737
188 | 20% | 5.329% | 25.33% | 0.064154 | 83.5378
189 | 20% | 5.181% | 25.18% | 0.06341 | 83.6012
190 | 20% | 5.038% | 25.04% | 0.062689 | 83.6639
191 | 20% | 4.898% | 24.9% | 0.061992 | 83.7259
192 | 20% | 4.762% | 24.76% | 0.061315 | 83.7872
193 | 20% | 4.629% | 24.63% | 0.060661 | 83.8479
194 | 20% | 4.5% | 24.5% | 0.060026 | 83.9079
195 | 20% | 4.375% | 24.37% | 0.059412 | 83.9673
196 | 20% | 4.252% | 24.25% | 0.058816 | 84.0262
197 | 20% | 4.133% | 24.13% | 0.05824 | 84.0844
198 | 20% | 4.017% | 24.02% | 0.057681 | 84.1421
199 | 20% | 3.904% | 23.9% | 0.05714 | 84.1992
200 | 20% | 3.794% | 23.79% | 0.056616 | 84.2558
201 | 20% | 3.687% | 23.69% | 0.056108 | 84.3119
202 | 20% | 3.583% | 23.58% | 0.055616 | 84.3676
203 | 20% | 3.482% | 23.48% | 0.055139 | 84.4227
204 | 20% | 3.383% | 23.38% | 0.054677 | 84.4774
205 | 20% | 3.287% | 23.29% | 0.05423 | 84.5316
206 | 20% | 3.194% | 23.19% | 0.053796 | 84.5854
207 | 20% | 3.103% | 23.1% | 0.053376 | 84.6388
208 | 20% | 3.015% | 23.02% | 0.052969 | 84.6917
209 | 20% | 2.929% | 22.93% | 0.052575 | 84.7443
210 | 20% | 2.846% | 22.85% | 0.052193 | 84.7965
211 | 20% | 2.764% | 22.76% | 0.051822 | 84.8483
212 | 20% | 2.686% | 22.69% | 0.051463 | 84.8998
213 | 20% | 2.609% | 22.61% | 0.051116 | 84.9509
214 | 20% | 2.534% | 22.53% | 0.050779 | 85.0017
215 | 20% | 2.462% | 22.46% | 0.050452 | 85.0521
216 | 20% | 2.391% | 22.39% | 0.050135 | 85.1023
217 | 20% | 2.322% | 22.32% | 0.049829 | 85.1521
218 | 20% | 2.256% | 22.26% | 0.049531 | 85.2016
219 | 20% | 2.191% | 22.19% | 0.049243 | 85.2509
220 | 20% | 2.128% | 22.13% | 0.048964 | 85.2998
221 | 20% | 2.066% | 22.07% | 0.048693 | 85.3485
222 | 20% | 2.007% | 22.01% | 0.048431 | 85.397
223 | 20% | 1.949% | 21.95% | 0.048176 | 85.4451
224 | 20% | 1.893% | 21.89% | 0.04793 | 85.4931
225 | 20% | 1.838% | 21.84% | 0.047691 | 85.5408
226 | 20% | 1.785% | 21.79% | 0.047459 | 85.5882
227 | 20% | 1.733% | 21.73% | 0.047234 | 85.6355
228 | 20% | 1.683% | 21.68% | 0.047017 | 85.6825
229 | 20% | 1.635% | 21.63% | 0.046805 | 85.7293
230 | 20% | 1.587% | 21.59% | 0.046601 | 85.7759
231 | 20% | 1.541% | 21.54% | 0.046402 | 85.8223
232 | 20% | 1.497% | 21.5% | 0.04621 | 85.8685
233 | 20% | 1.453% | 21.45% | 0.046024 | 85.9145
234 | 20% | 1.411% | 21.41% | 0.045843 | 85.9604
235 | 20% | 1.37% | 21.37% | 0.045667 | 86.006
236 | 20% | 1.33% | 21.33% | 0.045497 | 86.0515
237 | 20% | 1.291% | 21.29% | 0.045333 | 86.0969
238 | 20% | 1.254% | 21.25% | 0.045173 | 86.142
239 | 20% | 1.217% | 21.22% | 0.045018 | 86.187
240 | 20% | 1.182% | 21.18% | 0.044867 | 86.2319
241 | 20% | 1.147% | 21.15% | 0.044722 | 86.2766
242 | 20% | 1.114% | 21.11% | 0.04458 | 86.3212
243 | 20% | 1.082% | 21.08% | 0.044443 | 86.3657
244 | 20% | 1.05% | 21.05% | 0.04431 | 86.41
245 | 20% | 1.019% | 21.02% | 0.044181 | 86.4542
246 | 20% | 0.9896% | 20.99% | 0.044056 | 86.4982
247 | 20% | 0.9607% | 20.96% | 0.043935 | 86.5421
248 | 20% | 0.9327% | 20.93% | 0.043818 | 86.586
249 | 20% | 0.9054% | 20.91% | 0.043704 | 86.6297
250 | 20% | 0.879% | 20.88% | 0.043593 | 86.6733
251 | 20% | 0.8533% | 20.85% | 0.043486 | 86.7167
252 | 20% | 0.8283% | 20.83% | 0.043382 | 86.7601
253 | 20% | 0.8041% | 20.8% | 0.043281 | 86.8034
254 | 20% | 0.7805% | 20.78% | 0.043183 | 86.8466
255 | 20% | 0.7577% | 20.76% | 0.043088 | 86.8897
256 | 20% | 0.7355% | 20.74% | 0.042996 | 86.9327
257 | 20% | 0.714% | 20.71% | 0.042907 | 86.9756
258 | 20% | 0.693% | 20.69% | 0.04282 | 87.0184
259 | 20% | 0.6727% | 20.67% | 0.042736 | 87.0611
260 | 20% | 0.653% | 20.65% | 0.042655 | 87.1038
261 | 20% | 0.6339% | 20.63% | 0.042576 | 87.1464
262 | 20% | 0.6153% | 20.62% | 0.042499 | 87.1889
263 | 20% | 0.5972% | 20.6% | 0.042425 | 87.2313
264 | 20% | 0.5797% | 20.58% | 0.042352 | 87.2736
265 | 20% | 0.5627% | 20.56% | 0.042282 | 87.3159
266 | 20% | 0.5462% | 20.55% | 0.042215 | 87.3581
267 | 20% | 0.5301% | 20.53% | 0.042149 | 87.4003
268 | 20% | 0.5146% | 20.51% | 0.042085 | 87.4424
269 | 20% | 0.4995% | 20.5% | 0.042023 | 87.4844
270 | 20% | 0.4848% | 20.48% | 0.041963 | 87.5264
271 | 20% | 0.4705% | 20.47% | 0.041904 | 87.5683
272 | 20% | 0.4567% | 20.46% | 0.041848 | 87.6101
273 | 20% | 0.4433% | 20.44% | 0.041793 | 87.6519
274 | 20% | 0.4303% | 20.43% | 0.04174 | 87.6936
275 | 20% | 0.4176% | 20.42% | 0.041688 | 87.7353
276 | 20% | 0.4053% | 20.41% | 0.041638 | 87.777
277 | 20% | 0.3934% | 20.39% | 0.041589 | 87.8186
278 | 20% | 0.3818% | 20.38% | 0.041542 | 87.8601
279 | 20% | 0.3706% | 20.37% | 0.041496 | 87.9016
280 | 20% | 0.3597% | 20.36% | 0.041452 | 87.943
281 | 20% | 0.3491% | 20.35% | 0.041409 | 87.9845
282 | 20% | 0.3388% | 20.34% | 0.041367 | 88.0258
283 | 20% | 0.3289% | 20.33% | 0.041326 | 88.0671
284 | 20% | 0.3192% | 20.32% | 0.041287 | 88.1084
285 | 20% | 0.3098% | 20.31% | 0.041249 | 88.1497
286 | 20% | 0.3007% | 20.3% | 0.041212 | 88.1909
287 | 20% | 0.2918% | 20.29% | 0.041176 | 88.2321
288 | 20% | 0.2832% | 20.28% | 0.041141 | 88.2732
289 | 20% | 0.2749% | 20.27% | 0.041107 | 88.3143
290 | 20% | 0.2668% | 20.27% | 0.041074 | 88.3554
291 | 20% | 0.2589% | 20.26% | 0.041042 | 88.3964
292 | 20% | 0.2513% | 20.25% | 0.041012 | 88.4374
293 | 20% | 0.2439% | 20.24% | 0.040982 | 88.4784
294 | 20% | 0.2367% | 20.24% | 0.040952 | 88.5194
295 | 20% | 0.2297% | 20.23% | 0.040924 | 88.5603
296 | 20% | 0.223% | 20.22% | 0.040897 | 88.6012
297 | 20% | 0.2164% | 20.22% | 0.04087 | 88.6421
298 | 20% | 0.21% | 20.21% | 0.040844 | 88.6829
299 | 20% | 0.2038% | 20.2% | 0.040819 | 88.7237
300 | 20% | 0.1978% | 20.2% | 0.040795 | 88.7645
301 | 20% | 0.192% | 20.19% | 0.040772 | 88.8053
302 | 20% | 0.1863% | 20.19% | 0.040749 | 88.8461
303 | 20% | 0.1808% | 20.18% | 0.040727 | 88.8868
304 | 20% | 0.1755% | 20.18% | 0.040705 | 88.9275
305 | 20% | 0.1703% | 20.17% | 0.040684 | 88.9682
306 | 20% | 0.1653% | 20.17% | 0.040664 | 89.0088
307 | 20% | 0.1604% | 20.16% | 0.040644 | 89.0495
308 | 20% | 0.1557% | 20.16% | 0.040625 | 89.0901
309 | 20% | 0.1511% | 20.15% | 0.040607 | 89.1307
310 | 20% | 0.1466% | 20.15% | 0.040589 | 89.1713
311 | 20% | 0.1423% | 20.14% | 0.040571 | 89.2119
312 | 20% | 0.1381% | 20.14% | 0.040554 | 89.2524
313 | 20% | 0.134% | 20.13% | 0.040538 | 89.293
314 | 20% | 0.1301% | 20.13% | 0.040522 | 89.3335
315 | 20% | 0.1262% | 20.13% | 0.040507 | 89.374
316 | 20% | 0.1225% | 20.12% | 0.040492 | 89.4145
317 | 20% | 0.1189% | 20.12% | 0.040477 | 89.455
318 | 20% | 0.1154% | 20.12% | 0.040463 | 89.4954
319 | 20% | 0.112% | 20.11% | 0.040449 | 89.5359
320 | 20% | 0.1087% | 20.11% | 0.040436 | 89.5763
321 | 20% | 0.1055% | 20.11% | 0.040423 | 89.6167
322 | 20% | 0.1024% | 20.1% | 0.04041 | 89.6571
323 | 20% | 0.09934% | 20.1% | 0.040398 | 89.6975
324 | 20% | 0.09641% | 20.1% | 0.040387 | 89.7379
325 | 20% | 0.09356% | 20.09% | 0.040375 | 89.7783
326 | 20% | 0.0908% | 20.09% | 0.040364 | 89.8187
327 | 20% | 0.08812% | 20.09% | 0.040353 | 89.859
328 | 20% | 0.08552% | 20.09% | 0.040343 | 89.8994
329 | 20% | 0.08299% | 20.08% | 0.040333 | 89.9397
330 | 20% | 0.08054% | 20.08% | 0.040323 | 89.98
331 | 20% | 0.07816% | 20.08% | 0.040313 | 90.0203
332 | 20% | 0.07586% | 20.08% | 0.040304 | 90.0606
333 | 20% | 0.07362% | 20.07% | 0.040295 | 90.1009
334 | 20% | 0.07144% | 20.07% | 0.040286 | 90.1412
335 | 20% | 0.06933% | 20.07% | 0.040278 | 90.1815
336 | 20% | 0.06729% | 20.07% | 0.04027 | 90.2218
337 | 20% | 0.0653% | 20.07% | 0.040262 | 90.262
338 | 20% | 0.06337% | 20.06% | 0.040254 | 90.3023
339 | 20% | 0.0615% | 20.06% | 0.040246 | 90.3425
340 | 20% | 0.05968% | 20.06% | 0.040239 | 90.3828
341 | 20% | 0.05792% | 20.06% | 0.040232 | 90.423
342 | 20% | 0.05621% | 20.06% | 0.040225 | 90.4632
343 | 20% | 0.05455% | 20.05% | 0.040218 | 90.5034
344 | 20% | 0.05294% | 20.05% | 0.040212 | 90.5436
345 | 20% | 0.05137% | 20.05% | 0.040206 | 90.5839
346 | 20% | 0.04986% | 20.05% | 0.0402 | 90.6241
347 | 20% | 0.04838% | 20.05% | 0.040194 | 90.6642
348 | 20% | 0.04696% | 20.05% | 0.040188 | 90.7044
349 | 20% | 0.04557% | 20.05% | 0.040182 | 90.7446
350 | 20% | 0.04422% | 20.04% | 0.040177 | 90.7848
351 | 20% | 0.04292% | 20.04% | 0.040172 | 90.825
352 | 20% | 0.04165% | 20.04% | 0.040167 | 90.8651
353 | 20% | 0.04042% | 20.04% | 0.040162 | 90.9053
354 | 20% | 0.03922% | 20.04% | 0.040157 | 90.9455
355 | 20% | 0.03807% | 20.04% | 0.040152 | 90.9856
356 | 20% | 0.03694% | 20.04% | 0.040148 | 91.0258
357 | 20% | 0.03585% | 20.04% | 0.040144 | 91.0659
358 | 20% | 0.03479% | 20.03% | 0.040139 | 91.106
359 | 20% | 0.03376% | 20.03% | 0.040135 | 91.1462
360 | 20% | 0.03277% | 20.03% | 0.040131 | 91.1863
361 | 20% | 0.0318% | 20.03% | 0.040127 | 91.2264
362 | 20% | 0.03086% | 20.03% | 0.040124 | 91.2666
363 | 20% | 0.02995% | 20.03% | 0.04012 | 91.3067
364 | 20% | 0.02906% | 20.03% | 0.040116 | 91.3468
365 | 20% | 0.0282% | 20.03% | 0.040113 | 91.3869

## (5)
| World Average Price of Carbon: | 24.2714 | USD/tonne
Data last updated April, 01 2021 |  | https://carbonpricingdashboard.worldbank.org/map_data
Note: Nominal prices on April, 01 2021 Prices are not necessarily comparable between carbon pricing initiatives because of differences in the number of sectors covered and allocation methods applied, specific exemptions, and different compensation methods. Due to the dynamic approach to continuously improve data quality and fluctuating exchange rates, data of different years may not always be comparable and could be amended following new information from official government sources. In addition, data for a limited number of initiatives may be incomplete as they are in the process of being validated and will be updated following confirmation from official government sources.
Name of the initiative | Instrument Type | Jurisdiction Covered | Price_label_1_2020 | Price_rate_1_2020 | Price_label_2_2020 | Price_rate_2_2020 | Price_label_1_2021 | Price_rate_1_ 2021 | Price_label_2_2021 | Price_rate_2_2021
Alberta TIER | ETS | Alberta |  | 22.6295 |  |  |  | 31.8345
Alberta carbon tax | Carbon tax | Alberta
Argentina carbon tax | Carbon tax | Argentina | Most liquid fuels |  | Fuel oil, mineral coal and petroleum coke |  | Most liquid fuels | 5.543 | Fuel oil, mineral coal and petroleum coke
Australia CPM | ETS | Australia
Austria undecided | Undecided | Austria
BC GGIRCA | ETS | British Columbia | [5 empty] | 19.8965
BC carbon tax | Carbon tax | British Columbia |  | 30.1727 |  |  |  | 35.8138
Baja Calfornia carbon tax | Carbon tax | Baja California |  | 8.0256 |  |  |  | 8.317
Beijing pilot ETS | ETS | Beijing |  | 13.354 |  |  |  | 4.3233
Brazil undecided | Undecided | Brazil
California CaT | ETS | California |  | 16.89 |  |  |  | 17.94
Canada federal OBPS | ETS | Canada | [5 empty] | 31.8345
Canada federal fuel charge | Carbon tax | Canada | [5 empty] | 31.8345
Catalonia carbon tax | Carbon tax | Catalonia
Chile ETS | ETS | Chile
Chile carbon tax | Carbon tax | Chile |  | 5 |  |  |  | 5
China national ETS | ETS | China
Chongqing pilot ETS | ETS | Chongqing |  | 2.6875 |  |  |  | 3.7146
Colombia ETS | ETS | Colombia
Colombia carbon tax | Carbon tax | Colombia | [5 empty] | 5
Cote dIvoire carbon tax | Carbon tax | Cote dIvoire
Denmark carbon tax | Carbon tax | Denmark | Fossil fuels | 27.7 | F-gases | 23.4746 | Fossil fuels | 28.1408 | F-gases | 23.6477
EU ETS | ETS | EU, Norway, Iceland, Liechtenstein |  | 30.1435 |  |  |  | 49.7795
Estonia carbon tax | Carbon tax | Estonia | [5 empty] | 2.3492
Finland carbon tax | Carbon tax | Finland | Transport fuels | 72.2419 | Other fossil fuels | 61.7552 | Transport fuels | 72.8252 | Other fossil fuels | 62.2538
France carbon tax | Carbon tax | France |  | 6.9798 |  |  |  | 52.3872
Fujian pilot ETS | ETS | Fujian |  | 2.7681 |  |  |  | 1.2463
Germany ETS | ETS | Germany | [5 empty] | 29.365
Guangdong pilot ETS | ETS | Guangdong (except Shenzhen) |  | 4.1014 |  |  |  | 5.7157
Hawaii carbon tax | Carbon tax | Hawaii
Hubei pilot ETS | ETS | Hubei |  | 4.7121 |  |  |  | 4.4115
Iceland carbon tax | Carbon tax | Iceland | Fossil fuels | 30.0137 | F-gases | 8.8588 | Fossil fuels | 34.8349 | F-gases | 19.7926
Indonesia ETS | ETS | Indonesia
Ireland carbon tax | Carbon tax | Ireland | Transport fuels | 30.295 | Other fossil fuels | 23.3039 | Transport fuels | 39.3491
Jalisco carbon tax | Carbon tax | Jalisco
Japan ETS | ETS | Japan
Japan carbon tax | Carbon tax | Japan |  | 2.7592 |  |  |  | 2.6085
Kazakhstan ETS | ETS | Kazakhstan |  | 1.1554 |  |  |  | 1.1768
Korea ETS | ETS | Korea, Republic of |  | 18.7986 |  |  |  | 15.8926
Latvia carbon tax | Carbon tax | Latvia |  | 10.4867 |  |  |  | 14.0952
Liechtenstein carbon tax | Carbon tax | Liechtenstein | [5 empty] | 101.4746
Luxembourg carbon tax | Carbon tax | Luxembourg |  |  |  |  | Diesel fuel | 40.1243 | All fossil fuels | 23.492
Manitoba ETS | ETS | Manitoba | [5 empty] | 19.8965
Manitoba carbon tax | Carbon tax | Manitoba | [5 empty] | 19.8965
Massachusetts ETS | ETS | Massachusetts |  | 8.26 |  |  |  | 6.5
Mexico carbon tax | Carbon tax | Mexico | Upper | 2.7942 | Lower | 0.34532 | Upper | 3.1795 | Lower | 0.36497
Mexico pilot ETS | ETS | Mexico
Montenegro ETS | ETS | Montenegro | [5 empty] | 28.1904
Netherlands carbon tax | Carbon tax | Netherlands | [5 empty] | 35.238
New Brunswick ETS | ETS | New Brunswick | [5 empty] | 31.8345
New Brunswick carbon tax | Carbon tax | New Brunswick | [5 empty] | 31.8345
New Zealand ETS | ETS | New Zealand |  | 22.4525 |  |  |  | 25.7599
Newfoundland and Labrador PSS | ETS | Newfoundland and Labrador | [5 empty] | 23.8758
Newfoundland and Labrador carbon tax | Carbon tax | Newfoundland and Labrador | [5 empty] | 23.8758
Northwest Territories carbon tax | Carbon tax | Northwest Territories | [5 empty] | 23.8758
Norway carbon tax | Carbon tax | Norway | Upper | 57.1446 | Lower | 3.2504 | Upper | 69.3263 | Lower | 3.871
Nova Scotia CaT | ETS | Nova Scotia | [5 empty] | 19.6578
Ontario CaT | ETS | Ontario
Ontario EPS | ETS | Ontario
Oregon ETS | ETS | Oregon
Pakistan ETS | ETS | Pakistan
Pennsylvania ETS | ETS | Pennsylvania
Poland carbon tax | Carbon tax | Poland |  | 0.07584 |  |  |  | 0.078624
Portugal carbon tax | Carbon tax | Portugal |  | 27.5207 |  |  |  | 28.1904
Prince Edward Island carbon tax | Carbon tax | Prince Edward Island | [5 empty] | 23.8758
Quebec CaT | ETS | Quebec |  | 16.89 |  |  |  | 17.94
RGGI | ETS | RGGI |  | 5.94 |  |  |  | 8.69
Rio de Janeiro ETS | ETS | Rio de Janeiro
Saitama ETS | ETS | Saitama |  | 5.7285 |  |  |  | 5.4157
Sao Paolo ETS | ETS | Sao Paolo
Saskatchewan OBPS | ETS | Saskatchewan | [5 empty] | 31.8345
Senegal carbon tax | Carbon tax | Senegal
Shanghai pilot ETS | ETS | Shanghai |  | 5.9917 |  |  |  | 6.3152
Shenzhen pilot ETS | ETS | Shenzhen |  | 3.5206 |  |  |  | 1.12
Singapore carbon tax | Carbon tax | Singapore | [5 empty] | 3.7136
Slovenia carbon tax | Carbon tax | Slovenia | [5 empty] | 20.3206
South Africa carbon tax | Carbon tax | South Africa |  | 7.3764 |  |  |  | 9.1509
Spain carbon tax | Carbon tax | Spain | [5 empty] | 17.619
Sweden carbon tax | Carbon tax | Sweden |  | 133.2587 |  |  |  | 137.2432
Switzerland ETS | ETS | Switzerland |  | 19.7863 |  |  |  | 46.1031
Switzerland carbon tax | Carbon tax | Switzerland | [5 empty] | 101.4746
TCI-P ETS | ETS | TCI
Taiwan ETS | ETS | Taiwan
Tamaulipas carbon tax | Carbon tax | Tamaulipas | [5 empty] | 12.7202
Thailand undecided | ETS | Thailand
Tianjin pilot ETS | ETS | Tianjin |  | 3.7849 |  |  |  | 3.8044
Tokyo CaT | ETS | Tokyo |  | 5.7285 |  |  |  | 4.8741
Turkey ETS | ETS | Turkey
UK carbon price support | Carbon tax | United Kingdom | [5 empty] | 24.795
Ukraine ETS | ETS | Ukraine
Ukraine carbon tax | Carbon tax | Ukraine | [5 empty] | 0.35942
United Kingdom undecided | Undecided | United Kingdom
Vietnam ETS | ETS | Vietnam
Virginia ETS | ETS | Virginia
Washington ETS | ETS | Washington
Zacatecas carbon tax | Carbon tax | Zacatecas |  | 11.8024 |  |  |  | 12.2309
Average:

## About
Title: | U4E Total Cost of Ownership Calculation Spreadsheet (version 1.1)
Date: | 14 December 2021; updated on 4 October 2022
Introduction
The International Electrotechnical Commission (IEC) developed and published a methodology (IEC TS 60076-20 Annex A) for taking into account the future value of losses when purchasing a transformer called the "Total Cost of Ownership" (TCO). The two critical inputs to the TCO calculation are the A-factor (providing an estimate of the value of losses in the core) and the B-factor (an estimate of the value of losses in the windings). Companies purchasing transformers can calculate and give their A and B factors to transformer manufacturers when tendering for new units, and these factors will influence the design of the transformer, resulting in a more energy-efficient, economically-optimized transformer design for that company. The purpose of this spreadsheet is to help companies calculate appropriate A and B factors which can then enable the transformer procurement process to benefit from the use of the Total Cost of Ownership (TCO) purchasing practices, ultimately resulting in more energy-efficient (and cost-effective) transformers. Additionally, this spreadsheet adds a specific aspect which is not part of IEC TC 60076-20, users of the spreadsheet are given the option to add the future value of carbon emissions into their purchasing decision, augmenting the A and B values.
How to Use the Spreadsheet
The TCO tab on the far left is where the total cost of ownership is calculated - this is the final output of the process, and it allows a comparison of several transformers of equivalent size and voltages, simply by inputting the purchase price and the watts of core and coil loss. Transformer procurement experts are encouraged to review the A-factor and B-factor tabs and check that the input assumptions being used in those sheets is representative of their utility of company. In addition, certain factors such as the load loss factor and energy value need can be customised to reflect the current national situation. This excel spreadsheet is accompanied by a written guide which explains the concept of TCO and transformer losses. Moreover, the guide includes a detailed explanation of the calculation of the A and B factors. The Inputs tab contains all the inputs that are used in the IEC TCO methodology, enabling utilities to fully customise the calculation to their specific economic environment.
Email: | unep-u4e@un.org
Tel: | +33 1 44 37 19 86
Copyright © United Nations Environment Programme, 2021
Disclaimer: The designations employed and the presentation of the material in this publication do not imply the expression of any opinion whatsoever on the part of the United Nations Environment Programme concerning the legal status of any country, territory, city or area or of its authorities, or concerning delimitation of its frontiers or boundaries. Moreover, the views expressed do not necessarily represent the decision or the stated policy of the United Nations Environment Programme, nor does citing of trade names or commercial processes constitute endorsement. The information contained within this publication may be subject to change without notice. While the authors have attempted to ensure that the information has been obtained from reliable sources, the United Nations Environment Programme is not responsible for any errors or omissions, or for the results obtained from the use of this information. All information is provided on an “as-is” basis with no guarantee of completeness, accuracy, timeliness or of the results obtained from the use of this information, and without warranty of any kind, express or implied, including, but not limited to warranties of performance, merchantability and fitness for a particular purpose. In no event will the United Nations Environment Programme, its related corporations, contributors, or the partners, agents or their respective employees have any liability to you or anyone else for any act and conduct in connection with or related to the information provided herein. This disclaimer applies to any damages or liability and in no event will the United Nations Environment Programme be liable to you for any indirect, consequential, exemplary, incidental or punitive damages, including lost profits, even if we have been advised of the possibility of such damages.

## Typical loss levels (hidden)
ABB Calculator | http://tcocalculator.abb.com/
DNVGL
Actom (South Africa) typical lossses | https://www.actom.co.za/wp-content/uploads/2016/10/Distribution-Transformers-Brochure.pdf

## IEA $-MWh (hidden)
https://www.iea.org/articles/levelised-cost-of-electricity-calculator
Levelised Cost of Electricity Calculator
Interactive table of LCOE estimates from Projected Costs of Generating Electricity 2020 ($/MWh)
Country | Category | Plant Type | Capital Costs | O&M | Fuel (th) | Fuel (el) | Carbon | CHP heat revenues | LCOE ($/MWh)
Italy | Bio | Biomass (0.45 MW) | 49.07 | 26.89 | 0 | 0 | 0 | 0 | 75.96
Italy | Bio | Biomass (0.42 MW) | 70.42 | 59 | 15.62 | 159.42 | 0 | 0 | 288.84 | Row Labels | Min of LCOE ($/MWh) | Max of LCOE ($/MWh)2 | Average of LCOE ($/MWh)3
India | Bio | Biomass (30.0 MW) | 9.34 | 2.24 | 47.81 | 106.24 | 0 | 0 | 117.82 | Bio | 53.52 | 288.84 | 134.035
Brazil | Bio | Biomass (25.0 MW) | 34.78 | 18.75 | 0 | 0 | 0 | 0 | 53.52 | CHP | 52.47 | 195.65 | 100.6392
Slovakia | CHP | Gas (OCGT/int. comb., CHP) (35.9 MW) | 10.82 | 6.1 | 27.3 | 57.46 | 12.75 | -26.13 | 61.01 | Coal | 70.54 | 146.49 | 102.582
Slovakia | CHP | Gas (CCGT, CHP) (5.8 MW) | 19.8 | 7.74 | 27.3 | 84.46 | 18.75 | -68.77 | 61.97 | Fuel cell | 158.07 | 237.03 | 195.6575
Romania | CHP | Gas (OCGT/int. comb., CHP) (195 MW) | 3.65 | 11.75 | 27.3 | 33.88 | 7.52 | -4.34 | 52.47 | Gas | 40.32 | 137.09 | 81.5827
Romania | CHP | Pulverised, lignite (CHP) (2900 MW) | 21.63 | 129.88 | 4 | 12.28 | 33.5 | -1.63 | 195.65 | Geothermal | 61.83 | 151.8 | 102.48
Italy | CHP | Biomass (CHP) (0.42 MW) | 70.42 | 59 | 15.62 | 154.82 | 0 | -114.61 | 169.62 | Hydro | 38.65 | 409.32 | 108.4683
Denmark | CHP | Ultra-supercritical (CHP) (700 MW) | 37.41 | 10.73 | 10.75 | 21.28 | 20.22 | -29.69 | 59.95 | Lignite | 92.86 | 115.99 | 101.93
Denmark | CHP | Gas (OCGT/int. comb., CHP) (125 MW) | 14.35 | 10.77 | 27.3 | 67.65 | 15.02 | -38.05 | 69.73 | Nuclear | 28.18 | 101.84 | 49.8494
Denmark | CHP | Gas (CCGT, CHP) (500 MW) | 17.78 | 11.96 | 27.3 | 47.47 | 10.54 | -14.82 | 72.92 | Solar | 33.94 | 274.57 | 98.9248
Denmark | CHP | Biomass (CHP) (258 MW) | 49.27 | 19.36 | 32.8 | 76.87 | 0 | -50.25 | 95.25 | Wind | 29.18 | 896 | 93.8986
Denmark | CHP | Biomass (CHP) (358 MW) | 42.37 | 14.28 | 41.18 | 95.07 | 0 | -39.01 | 112.72 | Grand Total | 28.18 | 896 | 96.1488
Denmark | CHP | Biomass (CHP) (177 MW) | 83.76 | 33.29 | 32.8 | 111.18 | 0 | -102.94 | 125.28
Denmark | CHP | Biomass (CHP) (261 MW) | 56.66 | 20.78 | 41.18 | 126.33 | 0 | -72.67 | 131.1
United States of America | Coal | Supercritical pulverised (650 MW) | 28.95 | 17.2 | 7.31 | 17.51 | 24.47 | 0 | 88.13
United States of America | Coal | Pulverised (650 MW) | 27.78 | 17.01 | 7.31 | 18.23 | 25.48 | 0 | 88.5 | Row Labels | Min of LCOE ($/MWh) | Average of LCOE ($/MWh)3 | Max of LCOE ($/MWh)2
United States of America | Coal | Pulverised (140 MW) | 38.65 | 22.25 | 7.31 | 20.36 | 28.46 | 0 | 109.72 | Bio | 53.52 | 134.035 | 288.84
United States of America | Coal | Supercritical pulverised (CCUS) (650 MW) | 52.18 | 30.15 | 7.31 | 22.38 | 12.51 | 0 | 117.23 | CHP | 52.47 | 100.6392 | 195.65
United States of America | Coal | Coal (641 MW) | 46.61 | 29.5 | 7.31 | 17.16 | 23.99 | 0 | 117.27 | Coal | 70.54 | 102.582 | 146.49
United States of America | Coal | Pulverised (CCUS) (650 MW) | 51.62 | 30.45 | 7.31 | 23.5 | 13.14 | 0 | 118.72 | Fuel cell | 158.07 | 195.6575 | 237.03
United States of America | Coal | Pulverised (138 MW) | 49.13 | 30.47 | 7.31 | 20.19 | 28.22 | 0 | 128.02 | Gas | 40.32 | 81.5827 | 137.09
United States of America | Coal | Coal (CCUS) (499 MW) | 67.17 | 42.96 | 7.31 | 23.32 | 13.04 | 0 | 146.49 | Geothermal | 61.83 | 102.48 | 151.8
Korea, Republic of | Coal | Ultra-supercritical (954 MW) | 12.9 | 11.62 | 11.89 | 27.47 | 23.6 | 0 | 75.59 | Hydro | 38.65 | 108.4683 | 409.32
Japan | Coal | Ultra-supercritical (749 MW) | 27.12 | 19.31 | 11.89 | 28.73 | 24.68 | 0 | 99.84 | Lignite | 92.86 | 101.93 | 115.99
India | Coal | Ultra-supercritical (pithead) (400 MW) | 12.87 | 8.53 | 11.89 | 26.43 | 22.7 | 0 | 70.54 | Nuclear | 28.18 | 49.8494 | 101.84
India | Coal | Ultra-supercritical (load centered) (400 MW) | 12.46 | 38.65 | 11.89 | 26.43 | 22.7 | 0 | 100.25 | Solar | 33.94 | 98.9248 | 274.57
China | Coal | Ultra-supercritical (347 MW) | 8.97 | 14.97 | 12.61 | 28.02 | 22.7 | 0 | 74.67 | Wind | 29.18 | 93.8986 | 896
Australia | Coal | Supercritical pulverised (722 MW) | 27.28 | 8.69 | 11.89 | 29.66 | 25.47 | 0 | 91.1 | Grand Total | 28.18 | 96.1488 | 896
Australia | Coal | Supercritical pulverised (CCUS) (633 MW) | 50.34 | 19.34 | 11.89 | 39.58 | 3.4 | 0 | 112.66
Norway | Fuel cell | Fuel cell (1.0 MW) | 45.26 | 1.69 | 50 | 111.11 | 0 | 0 | 158.07
France | Fuel cell | Fuel cell (15.2 MW) | 30.28 | 36.75 | 50 | 111.11 | 0 | 0 | 178.14
France | Fuel cell | Fuel cell (0.20 MW) | 75.69 | 22.59 | 50 | 111.11 | 0 | 0 | 209.39
France | Fuel cell | Fuel cell (0.003 MW) | 83.26 | 42.66 | 50 | 111.11 | 0 | 0 | 237.03
United States of America | Gas | Gas (CCGT) (727 MW) | 11.1 | 5.3 | 10.92 | 18.38 | 10.2 | 0 | 44.98
United States of America | Gas | Gas (CCGT, CCUS) (646 MW) | 28.13 | 14.22 | 10.92 | 22.91 | 5.09 | 0 | 70.34
Romania | Gas | Gas (CCGT) (750 MW) | 3.01 | 46.27 | 27.3 | 47.06 | 10.45 | 0 | 106.79
Mexico | Gas | Gas (CCGT) (835 MW) | 5.44 | 5.51 | 10.92 | 18.89 | 10.48 | 0 | 40.32
Mexico | Gas | Gas (CCGT) (785 MW) | 7.78 | 5.73 | 10.92 | 18.29 | 10.15 | 0 | 41.95
Mexico | Gas | Gas (CCGT) (503 MW) | 7.81 | 5.28 | 10.92 | 21.62 | 12 | 0 | 46.71
Korea, Republic of | Gas | Gas (CCGT) (982 MW) | 9.78 | 8.41 | 34.12 | 58.23 | 10.34 | 0 | 86.76
Korea, Republic of | Gas | Gas (CCGT) (491 MW) | 12.91 | 11.36 | 34.12 | 60.82 | 10.8 | 0 | 95.89
Japan | Gas | Gas (CCGT) (1372 MW) | 12.93 | 7.7 | 34.12 | 61.04 | 10.84 | 0 | 92.52
Italy | Gas | Gas (CCGT) (790 MW) | 6.88 | 6.99 | 27.3 | 45.5 | 10.1 | 0 | 69.47
Italy | Gas | Gas (OCGT/int. comb.) (130 MW) | 10.36 | 11.11 | 27.3 | 73.98 | 16.42 | 0 | 111.87
China | Gas | Gas (CCGT) (475 MW) | 6.53 | 13.49 | 31.05 | 53.53 | 10.45 | 0 | 84
Canada | Gas | Gas (CCGT) (471 MW) | 12.34 | 6.96 | 10.92 | 19.19 | 10.65 | 0 | 49.13
Canada | Gas | Gas (OCGT/int. comb.) (243 MW) | 16.53 | 18.53 | 10.92 | 27.3 | 15.15 | 0 | 77.5
Canada | Gas | Gas (OCGT/int. comb.) (100 MW) | 36.41 | 8.7 | 10.92 | 26.44 | 14.67 | 0 | 86.22
Brazil | Gas | Gas (CCGT) (980 MW) | 11.17 | 11.21 | 10.92 | 18.83 | 10.45 | 0 | 51.66
Brazil | Gas | Gas (OCGT/int. comb.) (980 MW) | 23.59 | 16.71 | 10.92 | 24.82 | 13.77 | 0 | 78.89
Belgium | Gas | Gas (CCGT) (500 MW) | 11.77 | 4.8 | 27.3 | 42.65 | 9.47 | 0 | 68.69
Belgium | Gas | Gas (CCGT) (500 MW) | 8.95 | 6 | 27.3 | 45.88 | 10.18 | 0 | 71
Belgium | Gas | Gas (CCGT) (500 MW) | 11.36 | 6.67 | 27.3 | 47.06 | 10.45 | 0 | 75.54
Belgium | Gas | Gas (OCGT/int. comb.) (350 MW) | 16.95 | 7.5 | 27.3 | 68.24 | 15.15 | 0 | 107.85
Belgium | Gas | Gas (OCGT/int. comb.) (500 MW) | 21.4 | 9.83 | 27.3 | 66.58 | 14.78 | 0 | 112.59
Belgium | Gas | Gas (OCGT/int. comb.) (500 MW) | 18.84 | 7.99 | 27.3 | 71.83 | 15.94 | 0 | 114.61
Australia | Gas | Gas (CCGT) (506 MW) | 11.14 | 6.59 | 26.63 | 56.04 | 12.75 | 0 | 86.51
Australia | Gas | Gas (CCGT, CCUS) (437 MW) | 32.96 | 12.87 | 26.63 | 64.96 | 1.48 | 0 | 112.27
Australia | Gas | Gas (OCGT/int. comb.) (537 MW) | 21.32 | 9.09 | 26.63 | 86.91 | 19.77 | 0 | 137.09
United States of America | Geothermal | Geothermal (30.0 MW) | 45.2 | 16.63 | 0 | 0 | 0 | 0 | 61.83
United States of America | Geothermal | Geothermal (25.0 MW) | 68.35 | 25.19 | 0 | 0 | 0 | 0 | 93.54
Italy | Geothermal | Geothermal (39.6 MW) | 50.17 | 17.96 | 0 | 0 | 0 | 0 | 68.13
Italy | Geothermal | Geothermal (15.0 MW) | 82.27 | 21.25 | 0 | 0 | 0 | 0 | 103.52
Italy | Geothermal | Geothermal (10.0 MW) | 113.04 | 23.02 | 0 | 0 | 0 | 0 | 136.06
Italy | Geothermal | Geothermal (5.0 MW) | 126.42 | 25.38 | 0 | 0 | 0 | 0 | 151.8
United States of America | Hydro | Run of river (>= 5 MW) (median case) (44.7 MW) | 62.25 | 8.33 | 0 | 0 | 0 | 0 | 70.58
United States of America | Hydro | Run of river (>= 5 MW) (median case) (94.0 MW) | 81.85 | 5.35 | 0 | 0 | 0 | 0 | 87.2
United States of America | Hydro | Run of river (>= 5 MW) (82.2 MW) | 84.28 | 5.93 | 0 | 0 | 0 | 0 | 90.21
United States of America | Hydro | Run of river (< 5 MW) (4.2 MW) | 66.1 | 24.42 | 0 | 0 | 0 | 0 | 90.52
United States of America | Hydro | Run of river (>= 5 MW) (44.1 MW) | 93.2 | 7.57 | 0 | 0 | 0 | 0 | 100.77
United States of America | Hydro | Run of river (< 5 MW) (4.8 MW) | 95.49 | 22.24 | 0 | 0 | 0 | 0 | 117.72
United States of America | Hydro | Run of river (< 5 MW) (3.7 MW) | 105.28 | 23.4 | 0 | 0 | 0 | 0 | 128.67
Norway | Hydro | Hydro reservoir (>= 5 MW) (30.0 MW) | 33.73 | 4.92 | 0 | 0 | 0 | 0 | 38.65
Norway | Hydro | Run of river (< 5 MW) (3.0 MW) | 38.59 | 8.61 | 0 | 0 | 0 | 0 | 47.19
Japan | Hydro | Hydro reservoir (>= 5 MW) (12.0 MW) | 119.4 | 23 | 0 | 0 | 0 | 0 | 142.4
Italy | Hydro | Run of river (< 5 MW) (0.50 MW) | 48.4 | 13.01 | 0 | 0 | 0 | 0 | 61.41
Italy | Hydro | Run of river (< 5 MW) (2.1 MW) | 58.95 | 8.42 | 0 | 0 | 0 | 0 | 67.38
Italy | Hydro | Run of river (< 5 MW) (1.0 MW) | 60.79 | 8.71 | 0 | 0 | 0 | 0 | 69.49
Italy | Hydro | Hydro reservoir (< 5 MW) (0.32 MW) | 55.94 | 16.85 | 0 | 0 | 0 | 0 | 72.79
Italy | Hydro | Run of river (< 5 MW) (0.69 MW) | 73.44 | 12.47 | 0 | 0 | 0 | 0 | 85.91
Italy | Hydro | Hydro reservoir (>= 5 MW) (15.0 MW) | 75.8 | 18.37 | 0 | 0 | 0 | 0 | 94.16
Italy | Hydro | Run of river (< 5 MW) (0.25 MW) | 75.5 | 22.09 | 0 | 0 | 0 | 0 | 97.59
Italy | Hydro | Run of river (< 5 MW) (0.10 MW) | 81.35 | 17.01 | 0 | 0 | 0 | 0 | 98.36
Italy | Hydro | Run of river (>= 5 MW) (5.0 MW) | 76.29 | 27.53 | 0 | 0 | 0 | 0 | 103.82
Italy | Hydro | Run of river (< 5 MW) (0.50 MW) | 100.69 | 12.07 | 0 | 0 | 0 | 0 | 112.76
Italy | Hydro | Run of river (< 5 MW) (0.19 MW) | 91.63 | 21.47 | 0 | 0 | 0 | 0 | 113.09
Italy | Hydro | Run of river (< 5 MW) (0.015 MW) | 108.43 | 24.64 | 0 | 0 | 0 | 0 | 133.08
Italy | Hydro | Run of river (< 5 MW) (0.50 MW) | 230.45 | 17.52 | 0 | 0 | 0 | 0 | 247.97
Italy | Hydro | Run of river (< 5 MW) (0.25 MW) | 228.56 | 29.18 | 0 | 0 | 0 | 0 | 257.75
Italy | Hydro | Run of river (< 5 MW) (0.25 MW) | 358.24 | 51.07 | 0 | 0 | 0 | 0 | 409.32
India | Hydro | Hydro reservoir (>= 5 MW) (175 MW) | 37.69 | 11.65 | 0 | 0 | 0 | 0 | 49.34
Germany | Hydro | Run of river (>= 5 MW) (24.5 MW) | 48.5 | 8.5 | 0 | 0 | 0 | 0 | 57
Brazil | Hydro | Run of river (>= 5 MW) (248 MW) | 42.96 | 3.16 | 0 | 0 | 0 | 0 | 46.12
Austria | Hydro | Run of river (< 5 MW) (2.2 MW) | 42.41 | 11.92 | 0 | 0 | 0 | 0 | 54.33
Brazil | Lignite | Coal (900 MW) | 24.55 | 8.6 | 10.8 | 31.76 | 32.03 | 0 | 96.94
Australia | Lignite | Supercritical pulverised (709 MW) | 42.11 | 11.26 | 1.63 | 5.13 | 34.36 | 0 | 92.86
Australia | Lignite | Supercritical pulverised (CCUS) (570 MW) | 77.26 | 25.56 | 1.63 | 7.89 | 5.28 | 0 | 115.99
United States of America | Nuclear | LTO (20 years) (1000 MW) | 5.23 | 18.69 | 0 | 9.33 | 0 | 0 | 33.25
United States of America | Nuclear | LTO (10 years) (1000 MW) | 8.02 | 18.69 | 0 | 9.33 | 0 | 0 | 36.04
United States of America | Nuclear | LWR (1100 MW) | 50.32 | 11.6 | 0 | 9.33 | 0 | 0 | 71.25
Switzerland | Nuclear | LTO (20 years) (1000 MW) | 7.35 | 12.92 | 0 | 9.33 | 0 | 0 | 29.6
Switzerland | Nuclear | LTO (10 years) (1000 MW) | 11.29 | 12.92 | 0 | 9.33 | 0 | 0 | 33.53
Sweden | Nuclear | LTO (20 years) (1000 MW) | 5.93 | 12.92 | 0 | 9.33 | 0 | 0 | 28.18
Sweden | Nuclear | LTO (10 years) (1000 MW) | 9.11 | 12.92 | 0 | 9.33 | 0 | 0 | 31.36
Slovakia | Nuclear | Nuclear (1004 MW) | 82.8 | 9.71 | 0 | 9.33 | 0 | 0 | 101.84
Russian Federation | Nuclear | Gen III projects (1122 MW) | 26.88 | 10.15 | 0 | 4.99 | 0 | 0 | 42.02
Korea, Republic of | Nuclear | ALWR (1377 MW) | 25.54 | 18.44 | 0 | 9.33 | 0 | 0 | 53.3
Japan | Nuclear | ALWR (1152 MW) | 46.92 | 25.84 | 0 | 13.92 | 0 | 0 | 86.67
India | Nuclear | LWR (950 MW) | 32.89 | 5.43 | 0 | 9.33 | 0 | 0 | 47.64
France | Nuclear | LTO (20 years) (1000 MW) | 8.41 | 12.92 | 0 | 9.33 | 0 | 0 | 30.65
France | Nuclear | LTO (10 years) (1000 MW) | 12.91 | 12.92 | 0 | 9.33 | 0 | 0 | 35.15
France | Nuclear | Gen III projects (1650 MW) | 47.51 | 14.26 | 0 | 9.33 | 0 | 0 | 71.1
China | Nuclear | Nuclear (950 MW) | 29.6 | 26.42 | 0 | 10 | 0 | 0 | 66.01
United States of America | Solar | Solar PV (utility scale) (100 MW) | 30.39 | 4.2 | 0 | 0 | 0 | 0 | 34.59
United States of America | Solar | Solar PV (utility scale) (100 MW) | 33.44 | 4.62 | 0 | 0 | 0 | 0 | 38.06
United States of America | Solar | Solar PV (utility scale) (median case) (100 MW) | 38.87 | 5.38 | 0 | 0 | 0 | 0 | 44.25
United States of America | Solar | Solar PV (utility scale) (100 MW) | 41.9 | 5.79 | 0 | 0 | 0 | 0 | 47.69
United States of America | Solar | Solar PV (utility scale) (100 MW) | 48.28 | 6.68 | 0 | 0 | 0 | 0 | 54.96
United States of America | Solar | Solar PV (commercial) (0.30 MW) | 68.64 | 5.83 | 0 | 0 | 0 | 0 | 74.46
United States of America | Solar | Solar PV (commercial) (0.30 MW) | 74.28 | 6.31 | 0 | 0 | 0 | 0 | 80.59
United States of America | Solar | Solar PV (commercial) (median case) (0.30 MW) | 86.81 | 7.37 | 0 | 0 | 0 | 0 | 94.18
United States of America | Solar | Solar PV (commercial) (0.30 MW) | 92.59 | 7.86 | 0 | 0 | 0 | 0 | 100.45
United States of America | Solar | Solar thermal (CSP) (median case) (100 MW) | 100.24 | 12.1 | 0 | 0 | 0 | 0 | 112.34
United States of America | Solar | Solar PV (commercial) (0.30 MW) | 107.33 | 9.11 | 0 | 0 | 0 | 0 | 116.44
United States of America | Solar | Solar thermal (CSP) (100 MW) | 104.5 | 12.61 | 0 | 0 | 0 | 0 | 117.11
United States of America | Solar | Solar PV (residential) (median case) (0.005 MW) | 116.44 | 10.09 | 0 | 0 | 0 | 0 | 126.54
United States of America | Solar | Solar PV (residential) (0.005 MW) | 124.62 | 10.8 | 0 | 0 | 0 | 0 | 135.42
United States of America | Solar | Solar PV (residential) (0.005 MW) | 128.99 | 11.18 | 0 | 0 | 0 | 0 | 140.17
United States of America | Solar | Solar thermal (CSP) (100 MW) | 126.89 | 15.31 | 0 | 0 | 0 | 0 | 142.21
United States of America | Solar | Solar PV (residential) (0.005 MW) | 140.91 | 12.21 | 0 | 0 | 0 | 0 | 153.12
United States of America | Solar | Solar PV (residential) (0.005 MW) | 143.88 | 12.47 | 0 | 0 | 0 | 0 | 156.35
Norway | Solar | Solar PV (commercial) (0.30 MW) | 98.7 | 41.75 | 0 | 0 | 0 | 0 | 140.45
Netherlands | Solar | Solar PV (utility scale) (8.0 MW) | 59.81 | 20.16 | 0 | 0 | 0 | 0 | 79.97
Netherlands | Solar | Solar PV (floating) (8.0 MW) | 63.66 | 22.73 | 0 | 0 | 0 | 0 | 86.39
Netherlands | Solar | Solar PV (commercial) (0.20 MW) | 64.33 | 25.17 | 0 | 0 | 0 | 0 | 89.5
Korea, Republic of | Solar | Solar PV (utility scale) (3.0 MW) | 84.24 | 12.32 | 0 | 0 | 0 | 0 | 96.57
Korea, Republic of | Solar | Solar PV (commercial) (0.099 MW) | 85.23 | 12.91 | 0 | 0 | 0 | 0 | 98.13
Japan | Solar | Solar PV (utility scale) (2.0 MW) | 147.72 | 24.34 | 0 | 0 | 0 | 0 | 172.05
Japan | Solar | Solar PV (residential) (0.004 MW) | 200.4 | 22.91 | 0 | 0 | 0 | 0 | 223.3
Italy | Solar | Solar PV (utility scale) (0.83 MW) | 43.46 | 14.62 | 0 | 0 | 0 | 0 | 58.09
Italy | Solar | Solar PV (utility scale) (0.83 MW) | 35.36 | 27.59 | 0 | 0 | 0 | 0 | 62.96
Italy | Solar | Solar PV (commercial) (0.21 MW) | 54.46 | 16.52 | 0 | 0 | 0 | 0 | 70.98
Italy | Solar | Solar PV (commercial) (0.42 MW) | 75.46 | 18.28 | 0 | 0 | 0 | 0 | 93.74
Italy | Solar | Solar PV (commercial) (0.083 MW) | 80.49 | 21.09 | 0 | 0 | 0 | 0 | 101.58
Italy | Solar | Solar PV (residential) (0.005 MW) | 82.2 | 57.53 | 0 | 0 | 0 | 0 | 139.73
Italy | Solar | Solar PV (residential) (0.004 MW) | 109.75 | 164.82 | 0 | 0 | 0 | 0 | 274.57
India | Solar | Solar PV (utility scale) (35.0 MW) | 31.91 | 3.69 | 0 | 0 | 0 | 0 | 35.6
Hungary | Solar | Solar PV (utility scale) (20.0 MW) | 74.98 | 11.06 | 0 | 0 | 0 | 0 | 86.05
Hungary | Solar | Solar PV (commercial) (0.50 MW) | 83.94 | 20.34 | 0 | 0 | 0 | 0 | 104.28
Hungary | Solar | Solar PV (commercial) (0.050 MW) | 103.49 | 2.1 | 0 | 0 | 0 | 0 | 105.59
Hungary | Solar | Solar PV (residential) (0.004 MW) | 138.16 | 3.53 | 0 | 0 | 0 | 0 | 141.69
France | Solar | Solar PV (utility scale) (25.0 MW) | 30.42 | 3.52 | 0 | 0 | 0 | 0 | 33.94
France | Solar | Solar PV (commercial) (0.50 MW) | 49.67 | 24.31 | 0 | 0 | 0 | 0 | 73.98
France | Solar | Solar PV (residential) (0.010 MW) | 99.33 | 24.31 | 0 | 0 | 0 | 0 | 123.65
Denmark | Solar | Solar PV (utility scale) (8.0 MW) | 34.14 | 6.97 | 0 | 0 | 0 | 0 | 41.11
Denmark | Solar | Solar PV (utility scale) (8.0 MW) | 35.87 | 7.69 | 0 | 0 | 0 | 0 | 43.56
Denmark | Solar | Solar PV (commercial) (0.10 MW) | 66.66 | 11.1 | 0 | 0 | 0 | 0 | 77.76
Denmark | Solar | Solar PV (residential) (0.006 MW) | 100.22 | 14.1 | 0 | 0 | 0 | 0 | 114.32
China | Solar | Solar PV (utility scale) (20.0 MW) | 42.76 | 8.02 | 0 | 0 | 0 | 0 | 50.78
Canada | Solar | Solar PV (utility scale) (20.0 MW) | 55.85 | 6.62 | 0 | 0 | 0 | 0 | 62.47
Canada | Solar | Solar PV (utility scale) (20.0 MW) | 68.59 | 19.36 | 0 | 0 | 0 | 0 | 87.94
Brazil | Solar | Solar PV (utility scale) (25.0 MW) | 39.5 | 6.52 | 0 | 0 | 0 | 0 | 46.02
Belgium | Solar | Solar PV (utility scale) (1.0 MW) | 77.43 | 12.78 | 0 | 0 | 0 | 0 | 90.22
Belgium | Solar | Solar PV (residential) (0.010 MW) | 81.35 | 21.13 | 0 | 0 | 0 | 0 | 102.48
Belgium | Solar | Solar PV (residential) (0.010 MW) | 112.23 | 13.65 | 0 | 0 | 0 | 0 | 125.88
Belgium | Solar | Solar PV (residential) (0.010 MW) | 143.81 | 15.34 | 0 | 0 | 0 | 0 | 159.15
Austria | Solar | Solar PV (residential) (0.020 MW) | 65 | 43.18 | 0 | 0 | 0 | 0 | 108.18
Australia | Solar | Solar PV (utility scale) (100 MW) | 33.86 | 4.79 | 0 | 0 | 0 | 0 | 38.65
Australia | Solar | Solar thermal (CSP) (150 MW) | 110.09 | 19.46 | 0 | 0 | 0 | 0 | 129.55
United States of America | Wind | Wind onshore (>= 1 MW) (100 MW) | 26.48 | 8.71 | 0 | 0 | 0 | 0 | 35.19
United States of America | Wind | Wind onshore (>= 1 MW) (100 MW) | 27.23 | 9.57 | 0 | 0 | 0 | 0 | 36.8
United States of America | Wind | Wind onshore (>= 1 MW) (100 MW) | 27.89 | 9.92 | 0 | 0 | 0 | 0 | 37.81
United States of America | Wind | Wind onshore (>= 1 MW) (median case) (100 MW) | 28.76 | 10.26 | 0 | 0 | 0 | 0 | 39.02
United States of America | Wind | Wind onshore (>= 1 MW) (100 MW) | 30.48 | 10.69 | 0 | 0 | 0 | 0 | 41.17
United States of America | Wind | Wind onshore (>= 1 MW) (100 MW) | 36.76 | 11.36 | 0 | 0 | 0 | 0 | 48.13
United States of America | Wind | Wind onshore (>= 1 MW) (100 MW) | 42.98 | 12.53 | 0 | 0 | 0 | 0 | 55.5
United States of America | Wind | Wind offshore (600 MW) | 45.26 | 14.11 | 0 | 0 | 0 | 0 | 59.37
United States of America | Wind | Wind offshore (600 MW) | 46.57 | 14.62 | 0 | 0 | 0 | 0 | 61.19
United States of America | Wind | Wind offshore (600 MW) | 40.91 | 20.44 | 0 | 0 | 0 | 0 | 61.35
United States of America | Wind | Wind offshore (600 MW) | 42.11 | 21.43 | 0 | 0 | 0 | 0 | 63.53
United States of America | Wind | Wind offshore (600 MW) | 48.72 | 15.49 | 0 | 0 | 0 | 0 | 64.21
United States of America | Wind | Wind offshore (median case) (600 MW) | 43.97 | 21.65 | 0 | 0 | 0 | 0 | 65.62
United States of America | Wind | Wind offshore (600 MW) | 46.12 | 21.95 | 0 | 0 | 0 | 0 | 68.07
United States of America | Wind | Wind offshore (600 MW) | 51.19 | 16.99 | 0 | 0 | 0 | 0 | 68.18
United States of America | Wind | Wind offshore (600 MW) | 47.7 | 22.92 | 0 | 0 | 0 | 0 | 70.63
United States of America | Wind | Wind onshore (>= 1 MW) (100 MW) | 59.15 | 14.15 | 0 | 0 | 0 | 0 | 73.29
United States of America | Wind | Wind offshore (600 MW) | 54.91 | 19.18 | 0 | 0 | 0 | 0 | 74.09
United States of America | Wind | Wind offshore (600 MW) | 56.08 | 26.32 | 0 | 0 | 0 | 0 | 82.4
United States of America | Wind | Wind onshore (>= 1 MW) (100 MW) | 76.39 | 16.49 | 0 | 0 | 0 | 0 | 92.88
United States of America | Wind | Wind offshore (600 MW) | 68.93 | 24.66 | 0 | 0 | 0 | 0 | 93.59
United States of America | Wind | Wind offshore (600 MW) | 79.22 | 32.56 | 0 | 0 | 0 | 0 | 111.78
United States of America | Wind | Wind offshore (600 MW) | 92.13 | 27.08 | 0 | 0 | 0 | 0 | 119.21
United States of America | Wind | Wind onshore (>= 1 MW) (100 MW) | 129.06 | 26.07 | 0 | 0 | 0 | 0 | 155.13
Russian Federation | Wind | Wind onshore (>= 1 MW) (280 MW) | 53.85 | 13.5 | 0 | 0 | 0 | 0 | 67.35
Russian Federation | Wind | Wind onshore (>= 1 MW) (60.0 MW) | 58.47 | 13.82 | 0 | 0 | 0 | 0 | 72.29
Norway | Wind | Wind onshore (>= 1 MW) (130 MW) | 20.92 | 9.84 | 0 | 0 | 0 | 0 | 30.76
Netherlands | Wind | Wind onshore (>= 1 MW) (50.0 MW) | 25.93 | 15.23 | 0 | 0 | 0 | 0 | 41.17
Korea, Republic of | Wind | Wind onshore (>= 1 MW) (14.9 MW) | 85.1 | 28.22 | 0 | 0 | 0 | 0 | 113.33
Korea, Republic of | Wind | Wind offshore (99.0 MW) | 115.89 | 45.1 | 0 | 0 | 0 | 0 | 160.99
Japan | Wind | Wind onshore (>= 1 MW) (20.0 MW) | 112.69 | 27.48 | 0 | 0 | 0 | 0 | 140.17
Japan | Wind | Wind offshore (100 MW) | 132.98 | 67.2 | 0 | 0 | 0 | 0 | 200.18
Italy | Wind | Wind onshore (>= 1 MW) (10.0 MW) | 37.96 | 14.91 | 0 | 0 | 0 | 0 | 52.87
Italy | Wind | Wind onshore (>= 1 MW) (20.0 MW) | 49.58 | 9.94 | 0 | 0 | 0 | 0 | 59.52
Italy | Wind | Wind onshore (< 1 MW) (0.90 MW) | 56 | 15.37 | 0 | 0 | 0 | 0 | 71.37
Italy | Wind | Wind onshore (< 1 MW) (0.80 MW) | 55.59 | 19.69 | 0 | 0 | 0 | 0 | 75.28
Italy | Wind | Wind onshore (< 1 MW) (0.90 MW) | 63.4 | 15.61 | 0 | 0 | 0 | 0 | 79.01
Italy | Wind | Wind onshore (< 1 MW) (0.83 MW) | 75.87 | 12.91 | 0 | 0 | 0 | 0 | 88.78
Italy | Wind | Wind onshore (>= 1 MW) (1.0 MW) | 76.88 | 14.56 | 0 | 0 | 0 | 0 | 91.44
Italy | Wind | Wind onshore (< 1 MW) (0.50 MW) | 78.55 | 20.38 | 0 | 0 | 0 | 0 | 98.94
Italy | Wind | Wind onshore (< 1 MW) (0.10 MW) | 106.61 | 29.29 | 0 | 0 | 0 | 0 | 135.9
Italy | Wind | Wind onshore (< 1 MW) (0.060 MW) | 136.39 | 39.28 | 0 | 0 | 0 | 0 | 175.67
Italy | Wind | Wind onshore (< 1 MW) (0.19 MW) | 157.47 | 27.55 | 0 | 0 | 0 | 0 | 185.02
Italy | Wind | Wind onshore (< 1 MW) (0.020 MW) | 170.23 | 41.87 | 0 | 0 | 0 | 0 | 212.1
Italy | Wind | Wind onshore (< 1 MW) (0.059 MW) | 199.74 | 41.46 | 0 | 0 | 0 | 0 | 241.2
Italy | Wind | Wind onshore (< 1 MW) (0.014 MW) | 304.25 | 591.74 | 0 | 0 | 0 | 0 | 896
India | Wind | Wind onshore (>= 1 MW) (65.0 MW) | 32.19 | 3.72 | 0 | 0 | 0 | 0 | 35.91
France | Wind | Wind onshore (>= 1 MW) (50.0 MW) | 38.35 | 17.73 | 0 | 0 | 0 | 0 | 56.08
France | Wind | Wind offshore (500 MW) | 67.36 | 22.46 | 0 | 0 | 0 | 0 | 89.82
Finland | Wind | Wind onshore (>= 1 MW) (30.0 MW) | 37.94 | 6.94 | 0 | 0 | 0 | 0 | 44.88
Denmark | Wind | Wind onshore (>= 1 MW) (4.5 MW) | 22.88 | 6.3 | 0 | 0 | 0 | 0 | 29.18
Denmark | Wind | Wind offshore (11.5 MW) | 32.76 | 12.33 | 0 | 0 | 0 | 0 | 45.09
Denmark | Wind | Wind offshore (11.3 MW) | 38.36 | 13.58 | 0 | 0 | 0 | 0 | 51.94
China | Wind | Wind onshore (>= 1 MW) (50.0 MW) | 45.25 | 13.18 | 0 | 0 | 0 | 0 | 58.43
China | Wind | Wind offshore (50.0 MW) | 63.18 | 18.68 | 0 | 0 | 0 | 0 | 81.86
Canada | Wind | Wind onshore (>= 1 MW) (200 MW) | 33.62 | 13.21 | 0 | 0 | 0 | 0 | 46.83
Brazil | Wind | Wind onshore (>= 1 MW) (30.0 MW) | 27.61 | 5.98 | 0 | 0 | 0 | 0 | 33.59
Belgium | Wind | Wind onshore (>= 1 MW) (30.0 MW) | 47.61 | 10.29 | 0 | 0 | 0 | 0 | 57.9
Belgium | Wind | Wind onshore (>= 1 MW) (30.0 MW) | 50.88 | 13.23 | 0 | 0 | 0 | 0 | 64.11
Belgium | Wind | Wind onshore (>= 1 MW) (5.0 MW) | 48.58 | 19.96 | 0 | 0 | 0 | 0 | 68.54
Belgium | Wind | Wind onshore (>= 1 MW) (4.5 MW) | 60.63 | 17.71 | 0 | 0 | 0 | 0 | 78.33
Belgium | Wind | Wind offshore (50.0 MW) | 59.79 | 27.64 | 0 | 0 | 0 | 0 | 87.43
Belgium | Wind | Wind offshore (12.0 MW) | 59.79 | 35.41 | 0 | 0 | 0 | 0 | 95.2
Austria | Wind | Wind onshore (>= 1 MW) (3.0 MW) | 52.74 | 23.61 | 0 | 0 | 0 | 0 | 76.35
Australia | Wind | Wind onshore (>= 1 MW) (100 MW) | 33.69 | 9.31 | 0 | 0 | 0 | 0 | 43
Australia | Wind | Wind offshore (100 MW) | 67.29 | 18.07 | 0 | 0 | 0 | 0 | 85.36